## 입고 TR #22 => SC #1
입출고대(22번 트랙-C/V#11) → S/C #1 입고작업 (시작 → 끝)
■ | 노란색 표시: 트랙번호와 실제 포트/슬롯 번호가 다른 주의 지점 — ① C/V#15 역순 슬롯(#30=_03) ② RGV To는 RGV측 포트 지정(도착 트랙 아님) ③ C/V#11 출고모드 전환 구간
# | 구간 | 주체 | 신호 / 설명 | 1호기 | 2호기 | 3호기 | 4호기 | 5호기 | 시스템 | 파일 | 함수
1 | CV #11 | EQP BIT ON | 입출고대 #22 적재 감지 (작업자 투입) | C/V #11 M037.1 %MX593 | C/V #11 M037.1 %MX593 | C/V #11 M037.1 %MX593 | C/V #11 M037.1 %MX593 | C/V #11 M037.1 %MX593
2 |  | EQP BIT ON | Load Complete #2 ON (적재 완료) | C/V #11 M036.4 %MX580 | C/V #11 M036.4 %MX580 | C/V #11 M036.4 %MX580 | C/V #11 M036.4 %MX580 | C/V #11 M036.4 %MX580
3 |  | WCS BIT ON | Load Complete Ack #2 ON (WCS) | C/V #11 M090.4 %MX1444 | C/V #11 M090.4 %MX1444 | C/V #11 M090.4 %MX1444 | C/V #11 M090.4 %MX1444 | C/V #11 M090.4 %MX1444 | EQP_TASK | CvThread.cs | CvEventCheck()
4 |  | EQP BIT OFF | Load Complete #2 OFF | C/V #11 M036.4 %MX580 | C/V #11 M036.4 %MX580 | C/V #11 M036.4 %MX580 | C/V #11 M036.4 %MX580 | C/V #11 M036.4 %MX580
5 |  | EQP BIT OFF | Load Complete Ack #2 OFF (설비 리셋) | C/V #11 M090.4 %MX1444 | C/V #11 M090.4 %MX1444 | C/V #11 M090.4 %MX1444 | C/V #11 M090.4 %MX1444 | C/V #11 M090.4 %MX1444
6 |  | WCS 값 | 방향 확인 - 입고 '0' | C/V #11 D0310 %DW490 | C/V #11 D0310 %DW490 | C/V #11 D0310 %DW490 | C/V #11 D0310 %DW490 | C/V #11 D0310 %DW490 | EQP_TASK IO_TASK | CvThread.cs cThread_SCH.cs | CvStatusScenario() RequestCvDirection()
7 |  | WCS 값 | JOB NO 최초 기록 (적재 위치) | C/V #11 R0102 %RB516 | C/V #11 R0102 %RB516 | C/V #11 R0102 %RB516 | C/V #11 R0102 %RB516 | C/V #11 R0102 %RB516 | EQP_TASK IO_TASK | CvThread.cs cThread_SCH.cs | CvTrackingWrite() DriveCV() → UpdateCvData()
8 |  | EQP BIT OFF | 적재 위치 Pallet Exist OFF (ID Shift) | C/V #11 M037.1 %MX593 | C/V #11 M037.1 %MX593 | C/V #11 M037.1 %MX593 | C/V #11 M037.1 %MX593 | C/V #11 M037.1 %MX593
9 |  | EQP BIT ON | 반출 위치 Pallet Exist ON (도착) | C/V #11 M037.0 %MX592 | C/V #11 M037.0 %MX592 | C/V #11 M037.0 %MX592 | C/V #11 M037.0 %MX592 | C/V #11 M037.0 %MX592
10 |  | WCS 값 | PLC ID Shift 결과 : JOB 이 반출 위치로 이동 | C/V #11 R0100 %RB512 | C/V #11 R0100 %RB512 | C/V #11 R0100 %RB512 | C/V #11 R0100 %RB512 | C/V #11 R0100 %RB512 | EQP_TASK | CvThread.cs | CvStatusScenario()
11 |  | EQP BIT ON | W.O 보고 (RGV Call) | C/V #11 M036.6 %MX582 | C/V #11 M036.6 %MX582 | C/V #11 M036.6 %MX582 | C/V #11 M036.6 %MX582 | C/V #11 M036.6 %MX582
12 |  | EQP BIT OFF | 반출 위치 Pallet Exist OFF (RGV Load 완료) | C/V #11 M037.0 %MX592 | C/V #11 M037.0 %MX592 | C/V #11 M037.0 %MX592 | C/V #11 M037.0 %MX592 | C/V #11 M037.0 %MX592
13 |  | EQP BIT ON | Unload Complete #1 ON (RGV 픽업) | C/V #11 M036.1 %MX577 | C/V #11 M036.1 %MX577 | C/V #11 M036.1 %MX577 | C/V #11 M036.1 %MX577 | C/V #11 M036.1 %MX577
14 |  | WCS BIT ON | Unload Complete Ack #1 ON (WCS) | C/V #11 M090.1 %MX1441 | C/V #11 M090.1 %MX1441 | C/V #11 M090.1 %MX1441 | C/V #11 M090.1 %MX1441 | C/V #11 M090.1 %MX1441 | EQP_TASK | CvThread.cs | CvEventCheck()
15 |  | EQP BIT OFF | Unload Complete #1 OFF | C/V #11 M036.1 %MX577 | C/V #11 M036.1 %MX577 | C/V #11 M036.1 %MX577 | C/V #11 M036.1 %MX577 | C/V #11 M036.1 %MX577
16 |  | EQP BIT OFF | Unload Complete Ack #1 OFF (설비 리셋) | C/V #11 M090.1 %MX1441 | C/V #11 M090.1 %MX1441 | C/V #11 M090.1 %MX1441 | C/V #11 M090.1 %MX1441 | C/V #11 M090.1 %MX1441
17 |  | EQP BIT OFF | W.O OFF | C/V #11 M036.6 %MX582 | C/V #11 M036.6 %MX582 | C/V #11 M036.6 %MX582 | C/V #11 M036.6 %MX582 | C/V #11 M036.6 %MX582
18 | RGV #1 | WCS 값 | IDLE=1 확인 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() PollObservations()
19 |  | WCS BIT ON | Transfer Command Req’ (WCS 지시) | RGV #1 M101.0 %MX1616 | RGV #1 M101.0 %MX1616 | RGV #1 M101.0 %MX1616 | RGV #1 M101.0 %MX1616 | RGV #1 M101.0 %MX1616 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() → UpdateRtvData() ConsumeCommands()
20 |  | WCS 값 | Transfer Command Data - From (픽업 포트) | RGV #1 D0370 %DW848 | RGV #1 D0370 %DW848 | RGV #1 D0370 %DW848 | RGV #1 D0370 %DW848 | RGV #1 D0370 %DW848 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() → UpdateRtvData() ConsumeCommands()
21 |  | WCS 값 | Transfer Command Data - To (통로 C/V RGV측 포트) | RGV #1 D0373 %DW851 | RGV #1 D0373 %DW851 | RGV #1 D0373 %DW851 | RGV #1 D0373 %DW851 | RGV #1 D0373 %DW851 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() → UpdateRtvData() ConsumeCommands()
22 |  | WCS 값 | Transfer Command Data - Job No | RGV #1 D0376 %DW854 | RGV #1 D0376 %DW854 | RGV #1 D0376 %DW854 | RGV #1 D0376 %DW854 | RGV #1 D0376 %DW854 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() → UpdateRtvData() ConsumeCommands()
23 |  | EQP BIT ON | Pallet Presence ON (RGV 적재) | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928
24 |  | WCS 값 | On RGV - 탑재 화물번호 | RGV #1 R0310 %RB1568 | RGV #1 R0310 %RB1568 | RGV #1 R0310 %RB1568 | RGV #1 R0310 %RB1568 | RGV #1 R0310 %RB1568 | EQP_TASK | VehThread.cs | PollObservations()
25 |  | EQP BIT ON | Load Complete ON | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944
26 |  | WCS BIT ON | Load Complete Ack ON (WCS) | RGV #1 M101.1 %MX1617 | RGV #1 M101.1 %MX1617 | RGV #1 M101.1 %MX1617 | RGV #1 M101.1 %MX1617 | RGV #1 M101.1 %MX1617 | EQP_TASK | VehThread.cs | PollObservations()
27 |  | WCS 값 | Transfer Complete Location | RGV #1 D0213 %DW339 | RGV #1 D0213 %DW339 | RGV #1 D0213 %DW339 | RGV #1 D0213 %DW339 | RGV #1 D0213 %DW339 | EQP_TASK IO_TASK | VehThread.cs cThread_SCH.cs | PollObservations() CompleteRGV()
28 |  | EQP BIT OFF | Load Complete OFF | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944
29 |  | EQP BIT OFF | Pallet Presence OFF (하역) | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928
30 |  | EQP BIT ON | Unload Complete ON | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945
31 |  | WCS BIT ON | Unload Complete Ack ON (WCS) | RGV #1 M101.2 %MX1618 | RGV #1 M101.2 %MX1618 | RGV #1 M101.2 %MX1618 | RGV #1 M101.2 %MX1618 | RGV #1 M101.2 %MX1618 | EQP_TASK | VehThread.cs | PollObservations()
32 |  | EQP BIT OFF | Unload Complete OFF | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945
33 |  | WCS 값 | IDLE 복귀 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | EQP_TASK IO_TASK | VehThread.cs cThread_SCH.cs | PollObservations() CompleteRGV()
34 | 통로 CV (CV #2, CV #4, CV #6, CV #8, CV #10) | EQP BIT ON | RGV측 Pallet Exist ON (RGV 하역 완료) | C/V #2 M019.0 %MX304 | C/V #4 M023.0 %MX368 | C/V #6 M027.0 %MX432 | C/V #8 M031.0 %MX496 | C/V #10 M035.0 %MX560
35 |  | EQP BIT ON | Load Complete #1 ON | C/V #2 M018.2 %MX290 | C/V #4 M022.2 %MX354 | C/V #6 M026.2 %MX418 | C/V #8 M030.2 %MX482 | C/V #10 M034.2 %MX546
36 |  | WCS BIT ON | Load Complete Ack #1 ON (WCS) | C/V #2 M081.2 %MX1298 | C/V #4 M083.2 %MX1330 | C/V #6 M085.2 %MX1362 | C/V #8 M087.2 %MX1394 | C/V #10 M089.2 %MX1426 | EQP_TASK | CvThread.cs | CvEventCheck()
37 |  | EQP BIT OFF | Load Complete #1 OFF | C/V #2 M018.2 %MX290 | C/V #4 M022.2 %MX354 | C/V #6 M026.2 %MX418 | C/V #8 M030.2 %MX482 | C/V #10 M034.2 %MX546
38 |  | WCS 값 | 방향 확인 - 입고 '0' | C/V #2 D0301 %DW481 | C/V #4 D0303 %DW483 | C/V #6 D0305 %DW485 | C/V #8 D0307 %DW487 | C/V #10 D0309 %DW489 | EQP_TASK IO_TASK | CvThread.cs cThread_SCH.cs | CvStatusScenario() RequestCvDirection()
39 |  | WCS 값 | JOB NO 기록 (RGV측 위치) | C/V #2 R0010 %RB32 | C/V #4 R0030 %RB96 | C/V #6 R0050 %RB160 | C/V #8 R0070 %RB224 | C/V #10 R0090 %RB288 | EQP_TASK IO_TASK | CvThread.cs cThread_SCH.cs | CvTrackingWrite() DriveCV() → UpdateCvData()
40 |  | EQP BIT OFF | RGV측 Pallet Exist OFF (ID Shift) | C/V #2 M019.0 %MX304 | C/V #4 M023.0 %MX368 | C/V #6 M027.0 %MX432 | C/V #8 M031.0 %MX496 | C/V #10 M035.0 %MX560
41 |  | EQP BIT ON | S/C측 Pallet Exist ON (도착) | C/V #2 M019.1 %MX305 | C/V #4 M023.1 %MX369 | C/V #6 M027.1 %MX433 | C/V #8 M031.1 %MX497 | C/V #10 M035.1 %MX561
42 |  | WCS 값 | PLC ID Shift 결과 : JOB 이 S/C측으로 이동 | C/V #2 R0012 %RB36 | C/V #4 R0032 %RB100 | C/V #6 R0052 %RB164 | C/V #8 R0072 %RB228 | C/V #10 R0092 %RB292 | EQP_TASK | CvThread.cs | CvStatusScenario()
43 |  | EQP BIT ON | W.O 보고 (S/C Call) | C/V #2 M018.6 %MX294 | C/V #4 M022.6 %MX358 | C/V #6 M026.6 %MX422 | C/V #8 M030.6 %MX486 | C/V #10 M034.6 %MX550
44 |  | EQP BIT OFF | S/C측 Pallet Exist OFF (S/C Load 완료) | C/V #2 M019.1 %MX305 | C/V #4 M023.1 %MX369 | C/V #6 M027.1 %MX433 | C/V #8 M031.1 %MX497 | C/V #10 M035.1 %MX561
45 |  | EQP BIT ON | Unload Complete #2 ON (S/C 픽업) | C/V #2 M018.3 %MX291 | C/V #4 M022.3 %MX355 | C/V #6 M026.3 %MX419 | C/V #8 M030.3 %MX483 | C/V #10 M034.3 %MX547
46 |  | WCS BIT ON | Unload Complete Ack #2 ON (WCS) | C/V #2 M081.3 %MX1299 | C/V #4 M083.3 %MX1331 | C/V #6 M085.3 %MX1363 | C/V #8 M087.3 %MX1395 | C/V #10 M089.3 %MX1427 | EQP_TASK | CvThread.cs | CvEventCheck()
47 |  | EQP BIT OFF | Unload Complete #2 OFF | C/V #2 M018.3 %MX291 | C/V #4 M022.3 %MX355 | C/V #6 M026.3 %MX419 | C/V #8 M030.3 %MX483 | C/V #10 M034.3 %MX547
48 |  | EQP BIT OFF | W.O OFF | C/V #2 M018.6 %MX294 | C/V #4 M022.6 %MX358 | C/V #6 M026.6 %MX422 | C/V #8 M030.6 %MX486 | C/V #10 M034.6 %MX550
49 | SC 반송 | WCS 값 | IDLE=1 확인 | S/C #1 D0160 %DW256 | S/C #2 D0170 %DW272 | S/C #3 D0180 %DW288 | S/C #4 D0190 %DW304 | S/C #5 D0200 %DW320 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() PollObservations()
50 |  | WCS BIT ON | Transfer Command Req’ (WCS 지시) | S/C #1 M096.0 %MX1536 | S/C #2 M097.0 %MX1552 | S/C #3 M098.0 %MX1568 | S/C #4 M099.0 %MX1584 | S/C #5 M100.0 %MX1600 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() → UpdateScData() ConsumeCommands()
51 |  | WCS 값 | Transfer Command Data - From (픽업 포트) | S/C #1 D0320 %DW768 | S/C #2 D0330 %DW784 | S/C #3 D0340 %DW800 | S/C #4 D0350 %DW816 | S/C #5 D0360 %DW832 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() → UpdateScData() ConsumeCommands()
52 |  | WCS 값 | Transfer Command Data - To (랙 셀(열/연/단)) | S/C #1 D0323 %DW771 | S/C #2 D0333 %DW787 | S/C #3 D0343 %DW803 | S/C #4 D0353 %DW819 | S/C #5 D0363 %DW835 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() → UpdateScData() ConsumeCommands()
53 |  | WCS 값 | Transfer Command Data - Job No | S/C #1 D0326 %DW774 | S/C #2 D0336 %DW790 | S/C #3 D0346 %DW806 | S/C #4 D0356 %DW822 | S/C #5 D0366 %DW838 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() → UpdateScData() ConsumeCommands()
54 |  | EQP BIT ON | Pallet Presence ON (S/C 적재) | S/C #1 M048.0 %MX768 | S/C #2 M050.0 %MX800 | S/C #3 M052.0 %MX832 | S/C #4 M054.0 %MX864 | S/C #5 M056.0 %MX896
55 |  | WCS 값 | On S/C - 탑재 화물번호 | S/C #1 R0300 %RB1536 | S/C #2 R0302 %RB1540 | S/C #3 R0304 %RB1544 | S/C #4 R0306 %RB1548 | S/C #5 R0308 %RB1552 | EQP_TASK | VehThread.cs | PollObservations()
56 |  | EQP BIT ON | Load Complete ON | S/C #1 M049.0 %MX784 | S/C #2 M051.0 %MX816 | S/C #3 M053.0 %MX848 | S/C #4 M055.0 %MX880 | S/C #5 M057.0 %MX912
57 |  | WCS BIT ON | Load Complete Ack ON (WCS) | S/C #1 M096.1 %MX1537 | S/C #2 M097.1 %MX1553 | S/C #3 M098.1 %MX1569 | S/C #4 M099.1 %MX1585 | S/C #5 M100.1 %MX1601 | EQP_TASK | VehThread.cs | PollObservations()
58 |  | WCS 값 | S/C 현재위치(열/연/단) | S/C #1 D0166 %DW262 | S/C #2 D0176 %DW278 | S/C #3 D0186 %DW294 | S/C #4 D0196 %DW310 | S/C #5 D0206 %DW326 | EQP_TASK | VehThread.cs | PollObservations()
59 |  | EQP BIT OFF | Load Complete OFF | S/C #1 M049.0 %MX784 | S/C #2 M051.0 %MX816 | S/C #3 M053.0 %MX848 | S/C #4 M055.0 %MX880 | S/C #5 M057.0 %MX912
60 |  | EQP BIT OFF | Pallet Presence OFF (랙 적치 완료) | S/C #1 M048.0 %MX768 | S/C #2 M050.0 %MX800 | S/C #3 M052.0 %MX832 | S/C #4 M054.0 %MX864 | S/C #5 M056.0 %MX896
61 |  | EQP BIT ON | Unload Complete ON | S/C #1 M049.1 %MX785 | S/C #2 M051.1 %MX817 | S/C #3 M053.1 %MX849 | S/C #4 M055.1 %MX881 | S/C #5 M057.1 %MX913
62 |  | WCS BIT ON | Unload Complete Ack ON (WCS) | S/C #1 M096.2 %MX1538 | S/C #2 M097.2 %MX1554 | S/C #3 M098.2 %MX1570 | S/C #4 M099.2 %MX1586 | S/C #5 M100.2 %MX1602 | EQP_TASK | VehThread.cs | PollObservations()
63 |  | WCS 값 | Transfer Complete Location | S/C #1 D0163 %DW259 | S/C #2 D0173 %DW275 | S/C #3 D0183 %DW291 | S/C #4 D0193 %DW307 | S/C #5 D0203 %DW323 | EQP_TASK IO_TASK | VehThread.cs cThread_SCH.cs | PollObservations() CompleteSC()
64 |  | EQP BIT OFF | Unload Complete OFF | S/C #1 M049.1 %MX785 | S/C #2 M051.1 %MX817 | S/C #3 M053.1 %MX849 | S/C #4 M055.1 %MX881 | S/C #5 M057.1 %MX913
65 |  | WCS 값 | IDLE 복귀 | S/C #1 D0160 %DW256 | S/C #2 D0170 %DW272 | S/C #3 D0180 %DW288 | S/C #4 D0190 %DW304 | S/C #5 D0200 %DW320 | EQP_TASK IO_TASK HOST_TASK | VehThread.cs cThread_SCH.cs CCliWork.cs | PollObservations() CompleteSC() GetJobCompleteReport()
반송 시나리오 1. 입출고대 #22 → S/C 입고 (C/V #11 → RGV → 통로 → S/C → 랙)
실선 → 비트 ON/OFF · 점선 → D/R 워드 값 기록·확인 · 왼쪽 끝 = M/D/R 영역 문서표기 + 실제 접근주소 (S/C #1 기준)
EQP (설비 / PLC)
ECS (WCS)
① C/V #11 — 17 스텝
M037.1 %MX593
1. 입출고대 #22 적재 감지 (작업자 투입)
M036.4 %MX580
2. Load Complete #2 ON (적재 완료)
M090.4 %MX1444
3. Load Complete Ack #2 ON (WCS)
M036.4 %MX580
4. Load Complete #2 OFF
M090.4 %MX1444
5. Load Complete Ack #2 OFF (설비 리셋)
D0310 %DW490
6. 방향 확인 - 입고 '0'
R0102 %RB516
7. JOB NO 최초 기록 (적재 위치)
M037.1 %MX593
8. 적재 위치 Pallet Exist OFF (ID Shift)
M037.0 %MX592
9. 반출 위치 Pallet Exist ON (도착)
R0100 %RB512
10. PLC ID Shift 결과 : JOB 이 반출 위치로 이동
M036.6 %MX582
11. W.O 보고 (RGV Call)
M037.0 %MX592
12. 반출 위치 Pallet Exist OFF (RGV Load 완료)
M036.1 %MX577
13. Unload Complete #1 ON (RGV 픽업)
M090.1 %MX1441
14. Unload Complete Ack #1 ON (WCS)
M036.1 %MX577
15. Unload Complete #1 OFF
M090.1 %MX1441
16. Unload Complete Ack #1 OFF (설비 리셋)
M036.6 %MX582
17. W.O OFF
② RGV #1 — 16 스텝
D0210 %DW336
18. IDLE=1 확인
M101.0 %MX1616
19. Transfer Command Req’ (WCS 지시)
D0370 %DW848
20. Transfer Command Data - From (픽업 포트)
D0373 %DW851
21. Transfer Command Data - To (통로 C/V RGV측 포트)
D0376 %DW854
22. Transfer Command Data - Job No
M058.0 %MX928
23. Pallet Presence ON (RGV 적재)
R0310 %RB1568
24. On RGV - 탑재 화물번호
M059.0 %MX944
25. Load Complete ON
M101.1 %MX1617
26. Load Complete Ack ON (WCS)
D0213 %DW339
27. Transfer Complete Location
M059.0 %MX944
28. Load Complete OFF
M058.0 %MX928
29. Pallet Presence OFF (하역)
M059.1 %MX945
30. Unload Complete ON
M101.2 %MX1618
31. Unload Complete Ack ON (WCS)
M059.1 %MX945
32. Unload Complete OFF
D0210 %DW336
33. IDLE 복귀
③ C/V #2 — 15 스텝
M019.0 %MX304
34. RGV측 Pallet Exist ON (RGV 하역 완료)
M018.2 %MX290
35. Load Complete #1 ON
M081.2 %MX1298
36. Load Complete Ack #1 ON (WCS)
M018.2 %MX290
37. Load Complete #1 OFF
D0301 %DW481
38. 방향 확인 - 입고 '0'
R0010 %RB32
39. JOB NO 기록 (RGV측 위치)
M019.0 %MX304
40. RGV측 Pallet Exist OFF (ID Shift)
M019.1 %MX305
41. S/C측 Pallet Exist ON (도착)
R0012 %RB36
42. PLC ID Shift 결과 : JOB 이 S/C측으로 이동
M018.6 %MX294
43. W.O 보고 (S/C Call)
M019.1 %MX305
44. S/C측 Pallet Exist OFF (S/C Load 완료)
M018.3 %MX291
45. Unload Complete #2 ON (S/C 픽업)
M081.3 %MX1299
46. Unload Complete Ack #2 ON (WCS)
M018.3 %MX291
47. Unload Complete #2 OFF
M018.6 %MX294
48. W.O OFF
④ S/C #1 — 17 스텝
D0160 %DW256
49. IDLE=1 확인
M096.0 %MX1536
50. Transfer Command Req’ (WCS 지시)
D0320 %DW768
51. Transfer Command Data - From (픽업 포트)
D0323 %DW771
52. Transfer Command Data - To (랙 셀(열/연/단))
D0326 %DW774
53. Transfer Command Data - Job No
M048.0 %MX768
54. Pallet Presence ON (S/C 적재)
R0300 %RB1536
55. On S/C - 탑재 화물번호
M049.0 %MX784
56. Load Complete ON
M096.1 %MX1537
57. Load Complete Ack ON (WCS)
D0166 %DW262
58. S/C 현재위치(열/연/단)
M049.0 %MX784
59. Load Complete OFF
M048.0 %MX768
60. Pallet Presence OFF (랙 적치 완료)
M049.1 %MX785
61. Unload Complete ON
M096.2 %MX1538
62. Unload Complete Ack ON (WCS)
D0163 %DW259
63. Transfer Complete Location
M049.1 %MX785
64. Unload Complete OFF
D0160 %DW256
65. IDLE 복귀

## 입고 TR #24 => SC #1
입고대(24번 트랙-C/V#12) → S/C #1 입고작업 (시작 → 끝)
■ | 노란색 표시: 트랙번호와 실제 포트/슬롯 번호가 다른 주의 지점 — ① C/V#15 역순 슬롯(#30=_03) ② RGV To는 RGV측 포트 지정(도착 트랙 아님) ③ C/V#11 출고모드 전환 구간
# | 구간 | 주체 | 신호 / 설명 | 1호기 | 2호기 | 3호기 | 4호기 | 5호기 | 시스템 | 파일 | 함수
1 | CV #12 | EQP BIT ON | 24 입고대 적재 감지 (작업자 투입) | C/V #12 M039.1 %MX625 | C/V #12 M039.1 %MX625 | C/V #12 M039.1 %MX625 | C/V #12 M039.1 %MX625 | C/V #12 M039.1 %MX625
2 |  | EQP BIT ON | Load Complete #2 ON (적재 완료) | C/V #12 M038.4 %MX612 | C/V #12 M038.4 %MX612 | C/V #12 M038.4 %MX612 | C/V #12 M038.4 %MX612 | C/V #12 M038.4 %MX612
3 |  | WCS BIT ON | Load Complete Ack #2 ON (WCS) | C/V #12 M091.4 %MX1460 | C/V #12 M091.4 %MX1460 | C/V #12 M091.4 %MX1460 | C/V #12 M091.4 %MX1460 | C/V #12 M091.4 %MX1460 | EQP_TASK | CvThread.cs | CvEventCheck()
4 |  | EQP BIT OFF | Load Complete #2 OFF | C/V #12 M038.4 %MX612 | C/V #12 M038.4 %MX612 | C/V #12 M038.4 %MX612 | C/V #12 M038.4 %MX612 | C/V #12 M038.4 %MX612
5 |  | EQP BIT OFF | Load Complete Ack #2 OFF (설비 리셋) | C/V #12 M091.4 %MX1460 | C/V #12 M091.4 %MX1460 | C/V #12 M091.4 %MX1460 | C/V #12 M091.4 %MX1460 | C/V #12 M091.4 %MX1460
6 |  | WCS 값 | 방향 확인 - 입고 '0' | C/V #12 D0311 %DW491 | C/V #12 D0311 %DW491 | C/V #12 D0311 %DW491 | C/V #12 D0311 %DW491 | C/V #12 D0311 %DW491 | EQP_TASK IO_TASK | CvThread.cs cThread_SCH.cs | CvStatusScenario() RequestCvDirection()
7 |  | WCS 값 | JOB NO 최초 기록 (적재 위치) | C/V #12 R0112 %RB548 | C/V #12 R0112 %RB548 | C/V #12 R0112 %RB548 | C/V #12 R0112 %RB548 | C/V #12 R0112 %RB548 | EQP_TASK IO_TASK | CvThread.cs cThread_SCH.cs | CvTrackingWrite() DriveCV() → UpdateCvData()
8 |  | EQP BIT OFF | 적재 위치 Pallet Exist OFF (ID Shift) | C/V #12 M039.1 %MX625 | C/V #12 M039.1 %MX625 | C/V #12 M039.1 %MX625 | C/V #12 M039.1 %MX625 | C/V #12 M039.1 %MX625
9 |  | EQP BIT ON | 반출 위치 Pallet Exist ON (도착) | C/V #12 M039.0 %MX624 | C/V #12 M039.0 %MX624 | C/V #12 M039.0 %MX624 | C/V #12 M039.0 %MX624 | C/V #12 M039.0 %MX624
10 |  | WCS 값 | PLC ID Shift 결과 : JOB 이 반출 위치로 이동 | C/V #12 R0110 %RB544 | C/V #12 R0110 %RB544 | C/V #12 R0110 %RB544 | C/V #12 R0110 %RB544 | C/V #12 R0110 %RB544 | EQP_TASK | CvThread.cs | CvStatusScenario()
11 |  | EQP BIT ON | W.O 보고 (RGV Call) | C/V #12 M038.6 %MX614 | C/V #12 M038.6 %MX614 | C/V #12 M038.6 %MX614 | C/V #12 M038.6 %MX614 | C/V #12 M038.6 %MX614
12 |  | EQP BIT OFF | 반출 위치 Pallet Exist OFF (RGV Load 완료) | C/V #12 M039.0 %MX624 | C/V #12 M039.0 %MX624 | C/V #12 M039.0 %MX624 | C/V #12 M039.0 %MX624 | C/V #12 M039.0 %MX624
13 |  | EQP BIT ON | Unload Complete #1 ON (RGV 픽업) | C/V #12 M038.1 %MX609 | C/V #12 M038.1 %MX609 | C/V #12 M038.1 %MX609 | C/V #12 M038.1 %MX609 | C/V #12 M038.1 %MX609
14 |  | WCS BIT ON | Unload Complete Ack #1 ON (WCS) | C/V #12 M091.1 %MX1457 | C/V #12 M091.1 %MX1457 | C/V #12 M091.1 %MX1457 | C/V #12 M091.1 %MX1457 | C/V #12 M091.1 %MX1457 | EQP_TASK | CvThread.cs | CvEventCheck()
15 |  | EQP BIT OFF | Unload Complete #1 OFF | C/V #12 M038.1 %MX609 | C/V #12 M038.1 %MX609 | C/V #12 M038.1 %MX609 | C/V #12 M038.1 %MX609 | C/V #12 M038.1 %MX609
16 |  | EQP BIT OFF | Unload Complete Ack #1 OFF (설비 리셋) | C/V #12 M091.1 %MX1457 | C/V #12 M091.1 %MX1457 | C/V #12 M091.1 %MX1457 | C/V #12 M091.1 %MX1457 | C/V #12 M091.1 %MX1457
17 |  | EQP BIT OFF | W.O OFF | C/V #12 M038.6 %MX614 | C/V #12 M038.6 %MX614 | C/V #12 M038.6 %MX614 | C/V #12 M038.6 %MX614 | C/V #12 M038.6 %MX614
18 | RGV #1 | WCS 값 | IDLE=1 확인 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() PollObservations()
19 |  | WCS BIT ON | Transfer Command Req’ (WCS 지시) | RGV #1 M101.0 %MX1616 | RGV #1 M101.0 %MX1616 | RGV #1 M101.0 %MX1616 | RGV #1 M101.0 %MX1616 | RGV #1 M101.0 %MX1616 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() → UpdateRtvData() ConsumeCommands()
20 |  | WCS 값 | Transfer Command Data - From (픽업 포트) | RGV #1 D0370 %DW848 | RGV #1 D0370 %DW848 | RGV #1 D0370 %DW848 | RGV #1 D0370 %DW848 | RGV #1 D0370 %DW848 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() → UpdateRtvData() ConsumeCommands()
21 |  | WCS 값 | Transfer Command Data - To (통로 C/V RGV측 포트) | RGV #1 D0373 %DW851 | RGV #1 D0373 %DW851 | RGV #1 D0373 %DW851 | RGV #1 D0373 %DW851 | RGV #1 D0373 %DW851 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() → UpdateRtvData() ConsumeCommands()
22 |  | WCS 값 | Transfer Command Data - Job No | RGV #1 D0376 %DW854 | RGV #1 D0376 %DW854 | RGV #1 D0376 %DW854 | RGV #1 D0376 %DW854 | RGV #1 D0376 %DW854 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() → UpdateRtvData() ConsumeCommands()
23 |  | EQP BIT ON | Pallet Presence ON (RGV 적재) | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928
24 |  | WCS 값 | On RGV - 탑재 화물번호 | RGV #1 R0310 %RB1568 | RGV #1 R0310 %RB1568 | RGV #1 R0310 %RB1568 | RGV #1 R0310 %RB1568 | RGV #1 R0310 %RB1568 | EQP_TASK | VehThread.cs | PollObservations()
25 |  | EQP BIT ON | Load Complete ON | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944
26 |  | WCS BIT ON | Load Complete Ack ON (WCS) | RGV #1 M101.1 %MX1617 | RGV #1 M101.1 %MX1617 | RGV #1 M101.1 %MX1617 | RGV #1 M101.1 %MX1617 | RGV #1 M101.1 %MX1617 | EQP_TASK | VehThread.cs | PollObservations()
27 |  | WCS 값 | Transfer Complete Location | RGV #1 D0213 %DW339 | RGV #1 D0213 %DW339 | RGV #1 D0213 %DW339 | RGV #1 D0213 %DW339 | RGV #1 D0213 %DW339 | EQP_TASK IO_TASK | VehThread.cs cThread_SCH.cs | PollObservations() CompleteRGV()
28 |  | EQP BIT OFF | Load Complete OFF | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944
29 |  | EQP BIT OFF | Pallet Presence OFF (하역) | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928
30 |  | EQP BIT ON | Unload Complete ON | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945
31 |  | WCS BIT ON | Unload Complete Ack ON (WCS) | RGV #1 M101.2 %MX1618 | RGV #1 M101.2 %MX1618 | RGV #1 M101.2 %MX1618 | RGV #1 M101.2 %MX1618 | RGV #1 M101.2 %MX1618 | EQP_TASK | VehThread.cs | PollObservations()
32 |  | EQP BIT OFF | Unload Complete OFF | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945
33 |  | WCS 값 | IDLE 복귀 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | EQP_TASK IO_TASK | VehThread.cs cThread_SCH.cs | PollObservations() CompleteRGV()
34 | 통로 CV (CV #2, CV #4, CV #6, CV #8, CV #10) | EQP BIT ON | RGV측 Pallet Exist ON (RGV 하역 완료) | C/V #2 M019.0 %MX304 | C/V #4 M023.0 %MX368 | C/V #6 M027.0 %MX432 | C/V #8 M031.0 %MX496 | C/V #10 M035.0 %MX560
35 |  | EQP BIT ON | Load Complete #1 ON | C/V #2 M018.2 %MX290 | C/V #4 M022.2 %MX354 | C/V #6 M026.2 %MX418 | C/V #8 M030.2 %MX482 | C/V #10 M034.2 %MX546
36 |  | WCS BIT ON | Load Complete Ack #1 ON (WCS) | C/V #2 M081.2 %MX1298 | C/V #4 M083.2 %MX1330 | C/V #6 M085.2 %MX1362 | C/V #8 M087.2 %MX1394 | C/V #10 M089.2 %MX1426 | EQP_TASK | CvThread.cs | CvEventCheck()
37 |  | EQP BIT OFF | Load Complete #1 OFF | C/V #2 M018.2 %MX290 | C/V #4 M022.2 %MX354 | C/V #6 M026.2 %MX418 | C/V #8 M030.2 %MX482 | C/V #10 M034.2 %MX546
38 |  | WCS 값 | 방향 확인 - 입고 '0' | C/V #2 D0301 %DW481 | C/V #4 D0303 %DW483 | C/V #6 D0305 %DW485 | C/V #8 D0307 %DW487 | C/V #10 D0309 %DW489 | EQP_TASK IO_TASK | CvThread.cs cThread_SCH.cs | CvStatusScenario() RequestCvDirection()
39 |  | WCS 값 | JOB NO 기록 (RGV측 위치) | C/V #2 R0010 %RB32 | C/V #4 R0030 %RB96 | C/V #6 R0050 %RB160 | C/V #8 R0070 %RB224 | C/V #10 R0090 %RB288 | EQP_TASK IO_TASK | CvThread.cs cThread_SCH.cs | CvTrackingWrite() DriveCV() → UpdateCvData()
40 |  | EQP BIT OFF | RGV측 Pallet Exist OFF (ID Shift) | C/V #2 M019.0 %MX304 | C/V #4 M023.0 %MX368 | C/V #6 M027.0 %MX432 | C/V #8 M031.0 %MX496 | C/V #10 M035.0 %MX560
41 |  | EQP BIT ON | S/C측 Pallet Exist ON (도착) | C/V #2 M019.1 %MX305 | C/V #4 M023.1 %MX369 | C/V #6 M027.1 %MX433 | C/V #8 M031.1 %MX497 | C/V #10 M035.1 %MX561
42 |  | WCS 값 | PLC ID Shift 결과 : JOB 이 S/C측으로 이동 | C/V #2 R0012 %RB36 | C/V #4 R0032 %RB100 | C/V #6 R0052 %RB164 | C/V #8 R0072 %RB228 | C/V #10 R0092 %RB292 | EQP_TASK | CvThread.cs | CvStatusScenario()
43 |  | EQP BIT ON | W.O 보고 (S/C Call) | C/V #2 M018.6 %MX294 | C/V #4 M022.6 %MX358 | C/V #6 M026.6 %MX422 | C/V #8 M030.6 %MX486 | C/V #10 M034.6 %MX550
44 |  | EQP BIT OFF | S/C측 Pallet Exist OFF (S/C Load 완료) | C/V #2 M019.1 %MX305 | C/V #4 M023.1 %MX369 | C/V #6 M027.1 %MX433 | C/V #8 M031.1 %MX497 | C/V #10 M035.1 %MX561
45 |  | EQP BIT ON | Unload Complete #2 ON (S/C 픽업) | C/V #2 M018.3 %MX291 | C/V #4 M022.3 %MX355 | C/V #6 M026.3 %MX419 | C/V #8 M030.3 %MX483 | C/V #10 M034.3 %MX547
46 |  | WCS BIT ON | Unload Complete Ack #2 ON (WCS) | C/V #2 M081.3 %MX1299 | C/V #4 M083.3 %MX1331 | C/V #6 M085.3 %MX1363 | C/V #8 M087.3 %MX1395 | C/V #10 M089.3 %MX1427 | EQP_TASK | CvThread.cs | CvEventCheck()
47 |  | EQP BIT OFF | Unload Complete #2 OFF | C/V #2 M018.3 %MX291 | C/V #4 M022.3 %MX355 | C/V #6 M026.3 %MX419 | C/V #8 M030.3 %MX483 | C/V #10 M034.3 %MX547
48 |  | EQP BIT OFF | W.O OFF | C/V #2 M018.6 %MX294 | C/V #4 M022.6 %MX358 | C/V #6 M026.6 %MX422 | C/V #8 M030.6 %MX486 | C/V #10 M034.6 %MX550
49 | SC 반송 | WCS 값 | IDLE=1 확인 | S/C #1 D0160 %DW256 | S/C #2 D0170 %DW272 | S/C #3 D0180 %DW288 | S/C #4 D0190 %DW304 | S/C #5 D0200 %DW320 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() PollObservations()
50 |  | WCS BIT ON | Transfer Command Req’ (WCS 지시) | S/C #1 M096.0 %MX1536 | S/C #2 M097.0 %MX1552 | S/C #3 M098.0 %MX1568 | S/C #4 M099.0 %MX1584 | S/C #5 M100.0 %MX1600 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() → UpdateScData() ConsumeCommands()
51 |  | WCS 값 | Transfer Command Data - From (픽업 포트) | S/C #1 D0320 %DW768 | S/C #2 D0330 %DW784 | S/C #3 D0340 %DW800 | S/C #4 D0350 %DW816 | S/C #5 D0360 %DW832 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() → UpdateScData() ConsumeCommands()
52 |  | WCS 값 | Transfer Command Data - To (랙 셀(열/연/단)) | S/C #1 D0323 %DW771 | S/C #2 D0333 %DW787 | S/C #3 D0343 %DW803 | S/C #4 D0353 %DW819 | S/C #5 D0363 %DW835 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() → UpdateScData() ConsumeCommands()
53 |  | WCS 값 | Transfer Command Data - Job No | S/C #1 D0326 %DW774 | S/C #2 D0336 %DW790 | S/C #3 D0346 %DW806 | S/C #4 D0356 %DW822 | S/C #5 D0366 %DW838 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() → UpdateScData() ConsumeCommands()
54 |  | EQP BIT ON | Pallet Presence ON (S/C 적재) | S/C #1 M048.0 %MX768 | S/C #2 M050.0 %MX800 | S/C #3 M052.0 %MX832 | S/C #4 M054.0 %MX864 | S/C #5 M056.0 %MX896
55 |  | WCS 값 | On S/C - 탑재 화물번호 | S/C #1 R0300 %RB1536 | S/C #2 R0302 %RB1540 | S/C #3 R0304 %RB1544 | S/C #4 R0306 %RB1548 | S/C #5 R0308 %RB1552 | EQP_TASK | VehThread.cs | PollObservations()
56 |  | EQP BIT ON | Load Complete ON | S/C #1 M049.0 %MX784 | S/C #2 M051.0 %MX816 | S/C #3 M053.0 %MX848 | S/C #4 M055.0 %MX880 | S/C #5 M057.0 %MX912
57 |  | WCS BIT ON | Load Complete Ack ON (WCS) | S/C #1 M096.1 %MX1537 | S/C #2 M097.1 %MX1553 | S/C #3 M098.1 %MX1569 | S/C #4 M099.1 %MX1585 | S/C #5 M100.1 %MX1601 | EQP_TASK | VehThread.cs | PollObservations()
58 |  | WCS 값 | S/C 현재위치(열/연/단) | S/C #1 D0166 %DW262 | S/C #2 D0176 %DW278 | S/C #3 D0186 %DW294 | S/C #4 D0196 %DW310 | S/C #5 D0206 %DW326 | EQP_TASK | VehThread.cs | PollObservations()
59 |  | EQP BIT OFF | Load Complete OFF | S/C #1 M049.0 %MX784 | S/C #2 M051.0 %MX816 | S/C #3 M053.0 %MX848 | S/C #4 M055.0 %MX880 | S/C #5 M057.0 %MX912
60 |  | EQP BIT OFF | Pallet Presence OFF (랙 적치 완료) | S/C #1 M048.0 %MX768 | S/C #2 M050.0 %MX800 | S/C #3 M052.0 %MX832 | S/C #4 M054.0 %MX864 | S/C #5 M056.0 %MX896
61 |  | EQP BIT ON | Unload Complete ON | S/C #1 M049.1 %MX785 | S/C #2 M051.1 %MX817 | S/C #3 M053.1 %MX849 | S/C #4 M055.1 %MX881 | S/C #5 M057.1 %MX913
62 |  | WCS BIT ON | Unload Complete Ack ON (WCS) | S/C #1 M096.2 %MX1538 | S/C #2 M097.2 %MX1554 | S/C #3 M098.2 %MX1570 | S/C #4 M099.2 %MX1586 | S/C #5 M100.2 %MX1602 | EQP_TASK | VehThread.cs | PollObservations()
63 |  | WCS 값 | Transfer Complete Location | S/C #1 D0163 %DW259 | S/C #2 D0173 %DW275 | S/C #3 D0183 %DW291 | S/C #4 D0193 %DW307 | S/C #5 D0203 %DW323 | EQP_TASK IO_TASK | VehThread.cs cThread_SCH.cs | PollObservations() CompleteSC()
64 |  | EQP BIT OFF | Unload Complete OFF | S/C #1 M049.1 %MX785 | S/C #2 M051.1 %MX817 | S/C #3 M053.1 %MX849 | S/C #4 M055.1 %MX881 | S/C #5 M057.1 %MX913
65 |  | WCS 값 | IDLE 복귀 | S/C #1 D0160 %DW256 | S/C #2 D0170 %DW272 | S/C #3 D0180 %DW288 | S/C #4 D0190 %DW304 | S/C #5 D0200 %DW320 | EQP_TASK IO_TASK HOST_TASK | VehThread.cs cThread_SCH.cs CCliWork.cs | PollObservations() CompleteSC() GetJobCompleteReport()
반송 시나리오 3-1. 24 입고대 → S/C 입고 (C/V #12 → RGV → 통로 → S/C → 랙)
실선 → 비트 ON/OFF · 점선 → D/R 워드 값 기록·확인 · 왼쪽 끝 = M/D/R 영역 문서표기 + 실제 접근주소 (S/C #1 기준)
EQP (설비 / PLC)
ECS (WCS)
① C/V #12 — 17 스텝
M039.1 %MX625
1. 24 입고대 적재 감지 (작업자 투입)
M038.4 %MX612
2. Load Complete #2 ON (적재 완료)
M091.4 %MX1460
3. Load Complete Ack #2 ON (WCS)
M038.4 %MX612
4. Load Complete #2 OFF
M091.4 %MX1460
5. Load Complete Ack #2 OFF (설비 리셋)
D0311 %DW491
6. 방향 확인 - 입고 '0'
R0112 %RB548
7. JOB NO 최초 기록 (적재 위치)
M039.1 %MX625
8. 적재 위치 Pallet Exist OFF (ID Shift)
M039.0 %MX624
9. 반출 위치 Pallet Exist ON (도착)
R0110 %RB544
10. PLC ID Shift 결과 : JOB 이 반출 위치로 이동
M038.6 %MX614
11. W.O 보고 (RGV Call)
M039.0 %MX624
12. 반출 위치 Pallet Exist OFF (RGV Load 완료)
M038.1 %MX609
13. Unload Complete #1 ON (RGV 픽업)
M091.1 %MX1457
14. Unload Complete Ack #1 ON (WCS)
M038.1 %MX609
15. Unload Complete #1 OFF
M091.1 %MX1457
16. Unload Complete Ack #1 OFF (설비 리셋)
M038.6 %MX614
17. W.O OFF
② RGV #1 — 16 스텝
D0210 %DW336
18. IDLE=1 확인
M101.0 %MX1616
19. Transfer Command Req’ (WCS 지시)
D0370 %DW848
20. Transfer Command Data - From (픽업 포트)
D0373 %DW851
21. Transfer Command Data - To (통로 C/V RGV측 포트)
D0376 %DW854
22. Transfer Command Data - Job No
M058.0 %MX928
23. Pallet Presence ON (RGV 적재)
R0310 %RB1568
24. On RGV - 탑재 화물번호
M059.0 %MX944
25. Load Complete ON
M101.1 %MX1617
26. Load Complete Ack ON (WCS)
D0213 %DW339
27. Transfer Complete Location
M059.0 %MX944
28. Load Complete OFF
M058.0 %MX928
29. Pallet Presence OFF (하역)
M059.1 %MX945
30. Unload Complete ON
M101.2 %MX1618
31. Unload Complete Ack ON (WCS)
M059.1 %MX945
32. Unload Complete OFF
D0210 %DW336
33. IDLE 복귀
③ C/V #2 — 15 스텝
M019.0 %MX304
34. RGV측 Pallet Exist ON (RGV 하역 완료)
M018.2 %MX290
35. Load Complete #1 ON
M081.2 %MX1298
36. Load Complete Ack #1 ON (WCS)
M018.2 %MX290
37. Load Complete #1 OFF
D0301 %DW481
38. 방향 확인 - 입고 '0'
R0010 %RB32
39. JOB NO 기록 (RGV측 위치)
M019.0 %MX304
40. RGV측 Pallet Exist OFF (ID Shift)
M019.1 %MX305
41. S/C측 Pallet Exist ON (도착)
R0012 %RB36
42. PLC ID Shift 결과 : JOB 이 S/C측으로 이동
M018.6 %MX294
43. W.O 보고 (S/C Call)
M019.1 %MX305
44. S/C측 Pallet Exist OFF (S/C Load 완료)
M018.3 %MX291
45. Unload Complete #2 ON (S/C 픽업)
M081.3 %MX1299
46. Unload Complete Ack #2 ON (WCS)
M018.3 %MX291
47. Unload Complete #2 OFF
M018.6 %MX294
48. W.O OFF
④ S/C #1 — 17 스텝
D0160 %DW256
49. IDLE=1 확인
M096.0 %MX1536
50. Transfer Command Req’ (WCS 지시)
D0320 %DW768
51. Transfer Command Data - From (픽업 포트)
D0323 %DW771
52. Transfer Command Data - To (랙 셀(열/연/단))
D0326 %DW774
53. Transfer Command Data - Job No
M048.0 %MX768
54. Pallet Presence ON (S/C 적재)
R0300 %RB1536
55. On S/C - 탑재 화물번호
M049.0 %MX784
56. Load Complete ON
M096.1 %MX1537
57. Load Complete Ack ON (WCS)
D0166 %DW262
58. S/C 현재위치(열/연/단)
M049.0 %MX784
59. Load Complete OFF
M048.0 %MX768
60. Pallet Presence OFF (랙 적치 완료)
M049.1 %MX785
61. Unload Complete ON
M096.2 %MX1538
62. Unload Complete Ack ON (WCS)
D0163 %DW259
63. Transfer Complete Location
M049.1 %MX785
64. Unload Complete OFF
D0160 %DW256
65. IDLE 복귀

## 입고 TR #30 => SC #1
입고대(30번 트랙-C/V#15) → S/C #1 입고작업 (시작 → 끝)
■ | 노란색 표시: 트랙번호와 실제 포트/슬롯 번호가 다른 주의 지점 — ① C/V#15 역순 슬롯(#30=_03) ② RGV To는 RGV측 포트 지정(도착 트랙 아님) ③ C/V#11 출고모드 전환 구간
# | 구간 | 주체 | 신호 / 설명 | 1호기 | 2호기 | 3호기 | 4호기 | 5호기 | 시스템 | 파일 | 함수
1 | CV #15 | EQP BIT ON | 30 입고대(포트30) 적재 감지 (작업자 투입) - 구 ECS 슬롯배치: _03 | C/V #15 M045.2 %MX722 | C/V #15 M045.2 %MX722 | C/V #15 M045.2 %MX722 | C/V #15 M045.2 %MX722 | C/V #15 M045.2 %MX722
2 |  | EQP BIT ON | Load Complete #2 ON (적재 완료) | C/V #15 M044.4 %MX708 | C/V #15 M044.4 %MX708 | C/V #15 M044.4 %MX708 | C/V #15 M044.4 %MX708 | C/V #15 M044.4 %MX708
3 |  | WCS BIT ON | Load Complete Ack #2 ON (WCS) | C/V #15 M094.4 %MX1508 | C/V #15 M094.4 %MX1508 | C/V #15 M094.4 %MX1508 | C/V #15 M094.4 %MX1508 | C/V #15 M094.4 %MX1508 | EQP_TASK | CvThread.cs | CvEventCheck()
4 |  | EQP BIT OFF | Load Complete #2 OFF | C/V #15 M044.4 %MX708 | C/V #15 M044.4 %MX708 | C/V #15 M044.4 %MX708 | C/V #15 M044.4 %MX708 | C/V #15 M044.4 %MX708
5 |  | EQP BIT OFF | Load Complete Ack #2 OFF (설비 리셋) | C/V #15 M094.4 %MX1508 | C/V #15 M094.4 %MX1508 | C/V #15 M094.4 %MX1508 | C/V #15 M094.4 %MX1508 | C/V #15 M094.4 %MX1508
6 |  | WCS 값 | 방향 확인 - 입고 '0' | C/V #15 D0314 %DW494 | C/V #15 D0314 %DW494 | C/V #15 D0314 %DW494 | C/V #15 D0314 %DW494 | C/V #15 D0314 %DW494 | EQP_TASK IO_TASK | CvThread.cs cThread_SCH.cs | CvStatusScenario() RequestCvDirection()
7 |  | WCS 값 | JOB NO 최초 기록 (적재 위치) | C/V #15 R0144 %RB648 | C/V #15 R0144 %RB648 | C/V #15 R0144 %RB648 | C/V #15 R0144 %RB648 | C/V #15 R0144 %RB648 | EQP_TASK IO_TASK | CvThread.cs cThread_SCH.cs | CvTrackingWrite() DriveCV() → UpdateCvData()
8 |  | EQP BIT OFF | 적재 위치 Pallet Exist OFF (ID Shift) | C/V #15 M045.2 %MX722 | C/V #15 M045.2 %MX722 | C/V #15 M045.2 %MX722 | C/V #15 M045.2 %MX722 | C/V #15 M045.2 %MX722
9 |  | EQP BIT ON | 반출 위치(포트31=_01) Pallet Exist ON (도착) | C/V #15 M045.0 %MX720 | C/V #15 M045.0 %MX720 | C/V #15 M045.0 %MX720 | C/V #15 M045.0 %MX720 | C/V #15 M045.0 %MX720
10 |  | WCS 값 | PLC ID Shift 결과 : JOB 이 반출 위치로 이동 | C/V #15 R0140 %RB640 | C/V #15 R0140 %RB640 | C/V #15 R0140 %RB640 | C/V #15 R0140 %RB640 | C/V #15 R0140 %RB640 | EQP_TASK | CvThread.cs | CvStatusScenario()
11 |  | EQP BIT ON | W.O 보고 (RGV Call) | C/V #15 M044.6 %MX710 | C/V #15 M044.6 %MX710 | C/V #15 M044.6 %MX710 | C/V #15 M044.6 %MX710 | C/V #15 M044.6 %MX710
12 |  | EQP BIT OFF | 반출 위치 Pallet Exist OFF (RGV Load 완료) | C/V #15 M045.0 %MX720 | C/V #15 M045.0 %MX720 | C/V #15 M045.0 %MX720 | C/V #15 M045.0 %MX720 | C/V #15 M045.0 %MX720
13 |  | EQP BIT ON | Unload Complete #1 ON (RGV 픽업) | C/V #15 M044.1 %MX705 | C/V #15 M044.1 %MX705 | C/V #15 M044.1 %MX705 | C/V #15 M044.1 %MX705 | C/V #15 M044.1 %MX705
14 |  | WCS BIT ON | Unload Complete Ack #1 ON (WCS) | C/V #15 M094.1 %MX1505 | C/V #15 M094.1 %MX1505 | C/V #15 M094.1 %MX1505 | C/V #15 M094.1 %MX1505 | C/V #15 M094.1 %MX1505 | EQP_TASK | CvThread.cs | CvEventCheck()
15 |  | EQP BIT OFF | Unload Complete #1 OFF | C/V #15 M044.1 %MX705 | C/V #15 M044.1 %MX705 | C/V #15 M044.1 %MX705 | C/V #15 M044.1 %MX705 | C/V #15 M044.1 %MX705
16 |  | EQP BIT OFF | Unload Complete Ack #1 OFF (설비 리셋) | C/V #15 M094.1 %MX1505 | C/V #15 M094.1 %MX1505 | C/V #15 M094.1 %MX1505 | C/V #15 M094.1 %MX1505 | C/V #15 M094.1 %MX1505
17 |  | EQP BIT OFF | W.O OFF | C/V #15 M044.6 %MX710 | C/V #15 M044.6 %MX710 | C/V #15 M044.6 %MX710 | C/V #15 M044.6 %MX710 | C/V #15 M044.6 %MX710
18 | RGV #1 | WCS 값 | IDLE=1 확인 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() PollObservations()
19 |  | WCS BIT ON | Transfer Command Req’ (WCS 지시) | RGV #1 M101.0 %MX1616 | RGV #1 M101.0 %MX1616 | RGV #1 M101.0 %MX1616 | RGV #1 M101.0 %MX1616 | RGV #1 M101.0 %MX1616 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() → UpdateRtvData() ConsumeCommands()
20 |  | WCS 값 | Transfer Command Data - From (픽업 포트) | RGV #1 D0370 %DW848 | RGV #1 D0370 %DW848 | RGV #1 D0370 %DW848 | RGV #1 D0370 %DW848 | RGV #1 D0370 %DW848 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() → UpdateRtvData() ConsumeCommands()
21 |  | WCS 값 | Transfer Command Data - To (통로 C/V RGV측 포트) | RGV #1 D0373 %DW851 | RGV #1 D0373 %DW851 | RGV #1 D0373 %DW851 | RGV #1 D0373 %DW851 | RGV #1 D0373 %DW851 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() → UpdateRtvData() ConsumeCommands()
22 |  | WCS 값 | Transfer Command Data - Job No | RGV #1 D0376 %DW854 | RGV #1 D0376 %DW854 | RGV #1 D0376 %DW854 | RGV #1 D0376 %DW854 | RGV #1 D0376 %DW854 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() → UpdateRtvData() ConsumeCommands()
23 |  | EQP BIT ON | Pallet Presence ON (RGV 적재) | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928
24 |  | WCS 값 | On RGV - 탑재 화물번호 | RGV #1 R0310 %RB1568 | RGV #1 R0310 %RB1568 | RGV #1 R0310 %RB1568 | RGV #1 R0310 %RB1568 | RGV #1 R0310 %RB1568 | EQP_TASK | VehThread.cs | PollObservations()
25 |  | EQP BIT ON | Load Complete ON | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944
26 |  | WCS BIT ON | Load Complete Ack ON (WCS) | RGV #1 M101.1 %MX1617 | RGV #1 M101.1 %MX1617 | RGV #1 M101.1 %MX1617 | RGV #1 M101.1 %MX1617 | RGV #1 M101.1 %MX1617 | EQP_TASK | VehThread.cs | PollObservations()
27 |  | WCS 값 | Transfer Complete Location | RGV #1 D0213 %DW339 | RGV #1 D0213 %DW339 | RGV #1 D0213 %DW339 | RGV #1 D0213 %DW339 | RGV #1 D0213 %DW339 | EQP_TASK IO_TASK | VehThread.cs cThread_SCH.cs | PollObservations() CompleteRGV()
28 |  | EQP BIT OFF | Load Complete OFF | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944
29 |  | EQP BIT OFF | Pallet Presence OFF (하역) | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928
30 |  | EQP BIT ON | Unload Complete ON | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945
31 |  | WCS BIT ON | Unload Complete Ack ON (WCS) | RGV #1 M101.2 %MX1618 | RGV #1 M101.2 %MX1618 | RGV #1 M101.2 %MX1618 | RGV #1 M101.2 %MX1618 | RGV #1 M101.2 %MX1618 | EQP_TASK | VehThread.cs | PollObservations()
32 |  | EQP BIT OFF | Unload Complete OFF | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945
33 |  | WCS 값 | IDLE 복귀 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | EQP_TASK IO_TASK | VehThread.cs cThread_SCH.cs | PollObservations() CompleteRGV()
34 | 통로 CV (CV #2, CV #4, CV #6, CV #8, CV #10) | EQP BIT ON | RGV측 Pallet Exist ON (RGV 하역 완료) | C/V #2 M019.0 %MX304 | C/V #4 M023.0 %MX368 | C/V #6 M027.0 %MX432 | C/V #8 M031.0 %MX496 | C/V #10 M035.0 %MX560
35 |  | EQP BIT ON | Load Complete #1 ON | C/V #2 M018.2 %MX290 | C/V #4 M022.2 %MX354 | C/V #6 M026.2 %MX418 | C/V #8 M030.2 %MX482 | C/V #10 M034.2 %MX546
36 |  | WCS BIT ON | Load Complete Ack #1 ON (WCS) | C/V #2 M081.2 %MX1298 | C/V #4 M083.2 %MX1330 | C/V #6 M085.2 %MX1362 | C/V #8 M087.2 %MX1394 | C/V #10 M089.2 %MX1426 | EQP_TASK | CvThread.cs | CvEventCheck()
37 |  | EQP BIT OFF | Load Complete #1 OFF | C/V #2 M018.2 %MX290 | C/V #4 M022.2 %MX354 | C/V #6 M026.2 %MX418 | C/V #8 M030.2 %MX482 | C/V #10 M034.2 %MX546
38 |  | WCS 값 | 방향 확인 - 입고 '0' | C/V #2 D0301 %DW481 | C/V #4 D0303 %DW483 | C/V #6 D0305 %DW485 | C/V #8 D0307 %DW487 | C/V #10 D0309 %DW489 | EQP_TASK IO_TASK | CvThread.cs cThread_SCH.cs | CvStatusScenario() RequestCvDirection()
39 |  | WCS 값 | JOB NO 기록 (RGV측 위치) | C/V #2 R0010 %RB32 | C/V #4 R0030 %RB96 | C/V #6 R0050 %RB160 | C/V #8 R0070 %RB224 | C/V #10 R0090 %RB288 | EQP_TASK IO_TASK | CvThread.cs cThread_SCH.cs | CvTrackingWrite() DriveCV() → UpdateCvData()
40 |  | EQP BIT OFF | RGV측 Pallet Exist OFF (ID Shift) | C/V #2 M019.0 %MX304 | C/V #4 M023.0 %MX368 | C/V #6 M027.0 %MX432 | C/V #8 M031.0 %MX496 | C/V #10 M035.0 %MX560
41 |  | EQP BIT ON | S/C측 Pallet Exist ON (도착) | C/V #2 M019.1 %MX305 | C/V #4 M023.1 %MX369 | C/V #6 M027.1 %MX433 | C/V #8 M031.1 %MX497 | C/V #10 M035.1 %MX561
42 |  | WCS 값 | PLC ID Shift 결과 : JOB 이 S/C측으로 이동 | C/V #2 R0012 %RB36 | C/V #4 R0032 %RB100 | C/V #6 R0052 %RB164 | C/V #8 R0072 %RB228 | C/V #10 R0092 %RB292 | EQP_TASK | CvThread.cs | CvStatusScenario()
43 |  | EQP BIT ON | W.O 보고 (S/C Call) | C/V #2 M018.6 %MX294 | C/V #4 M022.6 %MX358 | C/V #6 M026.6 %MX422 | C/V #8 M030.6 %MX486 | C/V #10 M034.6 %MX550
44 |  | EQP BIT OFF | S/C측 Pallet Exist OFF (S/C Load 완료) | C/V #2 M019.1 %MX305 | C/V #4 M023.1 %MX369 | C/V #6 M027.1 %MX433 | C/V #8 M031.1 %MX497 | C/V #10 M035.1 %MX561
45 |  | EQP BIT ON | Unload Complete #2 ON (S/C 픽업) | C/V #2 M018.3 %MX291 | C/V #4 M022.3 %MX355 | C/V #6 M026.3 %MX419 | C/V #8 M030.3 %MX483 | C/V #10 M034.3 %MX547
46 |  | WCS BIT ON | Unload Complete Ack #2 ON (WCS) | C/V #2 M081.3 %MX1299 | C/V #4 M083.3 %MX1331 | C/V #6 M085.3 %MX1363 | C/V #8 M087.3 %MX1395 | C/V #10 M089.3 %MX1427 | EQP_TASK | CvThread.cs | CvEventCheck()
47 |  | EQP BIT OFF | Unload Complete #2 OFF | C/V #2 M018.3 %MX291 | C/V #4 M022.3 %MX355 | C/V #6 M026.3 %MX419 | C/V #8 M030.3 %MX483 | C/V #10 M034.3 %MX547
48 |  | EQP BIT OFF | W.O OFF | C/V #2 M018.6 %MX294 | C/V #4 M022.6 %MX358 | C/V #6 M026.6 %MX422 | C/V #8 M030.6 %MX486 | C/V #10 M034.6 %MX550
49 | SC 반송 | WCS 값 | IDLE=1 확인 | S/C #1 D0160 %DW256 | S/C #2 D0170 %DW272 | S/C #3 D0180 %DW288 | S/C #4 D0190 %DW304 | S/C #5 D0200 %DW320 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() PollObservations()
50 |  | WCS BIT ON | Transfer Command Req’ (WCS 지시) | S/C #1 M096.0 %MX1536 | S/C #2 M097.0 %MX1552 | S/C #3 M098.0 %MX1568 | S/C #4 M099.0 %MX1584 | S/C #5 M100.0 %MX1600 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() → UpdateScData() ConsumeCommands()
51 |  | WCS 값 | Transfer Command Data - From (픽업 포트) | S/C #1 D0320 %DW768 | S/C #2 D0330 %DW784 | S/C #3 D0340 %DW800 | S/C #4 D0350 %DW816 | S/C #5 D0360 %DW832 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() → UpdateScData() ConsumeCommands()
52 |  | WCS 값 | Transfer Command Data - To (랙 셀(열/연/단)) | S/C #1 D0323 %DW771 | S/C #2 D0333 %DW787 | S/C #3 D0343 %DW803 | S/C #4 D0353 %DW819 | S/C #5 D0363 %DW835 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() → UpdateScData() ConsumeCommands()
53 |  | WCS 값 | Transfer Command Data - Job No | S/C #1 D0326 %DW774 | S/C #2 D0336 %DW790 | S/C #3 D0346 %DW806 | S/C #4 D0356 %DW822 | S/C #5 D0366 %DW838 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() → UpdateScData() ConsumeCommands()
54 |  | EQP BIT ON | Pallet Presence ON (S/C 적재) | S/C #1 M048.0 %MX768 | S/C #2 M050.0 %MX800 | S/C #3 M052.0 %MX832 | S/C #4 M054.0 %MX864 | S/C #5 M056.0 %MX896
55 |  | WCS 값 | On S/C - 탑재 화물번호 | S/C #1 R0300 %RB1536 | S/C #2 R0302 %RB1540 | S/C #3 R0304 %RB1544 | S/C #4 R0306 %RB1548 | S/C #5 R0308 %RB1552 | EQP_TASK | VehThread.cs | PollObservations()
56 |  | EQP BIT ON | Load Complete ON | S/C #1 M049.0 %MX784 | S/C #2 M051.0 %MX816 | S/C #3 M053.0 %MX848 | S/C #4 M055.0 %MX880 | S/C #5 M057.0 %MX912
57 |  | WCS BIT ON | Load Complete Ack ON (WCS) | S/C #1 M096.1 %MX1537 | S/C #2 M097.1 %MX1553 | S/C #3 M098.1 %MX1569 | S/C #4 M099.1 %MX1585 | S/C #5 M100.1 %MX1601 | EQP_TASK | VehThread.cs | PollObservations()
58 |  | WCS 값 | S/C 현재위치(열/연/단) | S/C #1 D0166 %DW262 | S/C #2 D0176 %DW278 | S/C #3 D0186 %DW294 | S/C #4 D0196 %DW310 | S/C #5 D0206 %DW326 | EQP_TASK | VehThread.cs | PollObservations()
59 |  | EQP BIT OFF | Load Complete OFF | S/C #1 M049.0 %MX784 | S/C #2 M051.0 %MX816 | S/C #3 M053.0 %MX848 | S/C #4 M055.0 %MX880 | S/C #5 M057.0 %MX912
60 |  | EQP BIT OFF | Pallet Presence OFF (랙 적치 완료) | S/C #1 M048.0 %MX768 | S/C #2 M050.0 %MX800 | S/C #3 M052.0 %MX832 | S/C #4 M054.0 %MX864 | S/C #5 M056.0 %MX896
61 |  | EQP BIT ON | Unload Complete ON | S/C #1 M049.1 %MX785 | S/C #2 M051.1 %MX817 | S/C #3 M053.1 %MX849 | S/C #4 M055.1 %MX881 | S/C #5 M057.1 %MX913
62 |  | WCS BIT ON | Unload Complete Ack ON (WCS) | S/C #1 M096.2 %MX1538 | S/C #2 M097.2 %MX1554 | S/C #3 M098.2 %MX1570 | S/C #4 M099.2 %MX1586 | S/C #5 M100.2 %MX1602 | EQP_TASK | VehThread.cs | PollObservations()
63 |  | WCS 값 | Transfer Complete Location | S/C #1 D0163 %DW259 | S/C #2 D0173 %DW275 | S/C #3 D0183 %DW291 | S/C #4 D0193 %DW307 | S/C #5 D0203 %DW323 | EQP_TASK IO_TASK | VehThread.cs cThread_SCH.cs | PollObservations() CompleteSC()
64 |  | EQP BIT OFF | Unload Complete OFF | S/C #1 M049.1 %MX785 | S/C #2 M051.1 %MX817 | S/C #3 M053.1 %MX849 | S/C #4 M055.1 %MX881 | S/C #5 M057.1 %MX913
65 |  | WCS 값 | IDLE 복귀 | S/C #1 D0160 %DW256 | S/C #2 D0170 %DW272 | S/C #3 D0180 %DW288 | S/C #4 D0190 %DW304 | S/C #5 D0200 %DW320 | EQP_TASK IO_TASK HOST_TASK | VehThread.cs cThread_SCH.cs CCliWork.cs | PollObservations() CompleteSC() GetJobCompleteReport()
반송 시나리오 4-1. 30 입고대 → S/C 입고 (C/V #15 → RGV → 통로 → S/C → 랙)
실선 → 비트 ON/OFF · 점선 → D/R 워드 값 기록·확인 · 왼쪽 끝 = M/D/R 영역 문서표기 + 실제 접근주소 (S/C #1 기준)
EQP (설비 / PLC)
ECS (WCS)
① C/V #15 — 17 스텝
M045.2 %MX722
1. 30 입고대(포트30) 적재 감지 (작업자 투입) - 구 ECS 슬롯배치: _03
M044.4 %MX708
2. Load Complete #2 ON (적재 완료)
M094.4 %MX1508
3. Load Complete Ack #2 ON (WCS)
M044.4 %MX708
4. Load Complete #2 OFF
M094.4 %MX1508
5. Load Complete Ack #2 OFF (설비 리셋)
D0314 %DW494
6. 방향 확인 - 입고 '0'
R0144 %RB648
7. JOB NO 최초 기록 (적재 위치)
M045.2 %MX722
8. 적재 위치 Pallet Exist OFF (ID Shift)
M045.0 %MX720
9. 반출 위치(포트31=_01) Pallet Exist ON (도착)
R0140 %RB640
10. PLC ID Shift 결과 : JOB 이 반출 위치로 이동
M044.6 %MX710
11. W.O 보고 (RGV Call)
M045.0 %MX720
12. 반출 위치 Pallet Exist OFF (RGV Load 완료)
M044.1 %MX705
13. Unload Complete #1 ON (RGV 픽업)
M094.1 %MX1505
14. Unload Complete Ack #1 ON (WCS)
M044.1 %MX705
15. Unload Complete #1 OFF
M094.1 %MX1505
16. Unload Complete Ack #1 OFF (설비 리셋)
M044.6 %MX710
17. W.O OFF
② RGV #1 — 16 스텝
D0210 %DW336
18. IDLE=1 확인
M101.0 %MX1616
19. Transfer Command Req’ (WCS 지시)
D0370 %DW848
20. Transfer Command Data - From (픽업 포트)
D0373 %DW851
21. Transfer Command Data - To (통로 C/V RGV측 포트)
D0376 %DW854
22. Transfer Command Data - Job No
M058.0 %MX928
23. Pallet Presence ON (RGV 적재)
R0310 %RB1568
24. On RGV - 탑재 화물번호
M059.0 %MX944
25. Load Complete ON
M101.1 %MX1617
26. Load Complete Ack ON (WCS)
D0213 %DW339
27. Transfer Complete Location
M059.0 %MX944
28. Load Complete OFF
M058.0 %MX928
29. Pallet Presence OFF (하역)
M059.1 %MX945
30. Unload Complete ON
M101.2 %MX1618
31. Unload Complete Ack ON (WCS)
M059.1 %MX945
32. Unload Complete OFF
D0210 %DW336
33. IDLE 복귀
③ C/V #2 — 15 스텝
M019.0 %MX304
34. RGV측 Pallet Exist ON (RGV 하역 완료)
M018.2 %MX290
35. Load Complete #1 ON
M081.2 %MX1298
36. Load Complete Ack #1 ON (WCS)
M018.2 %MX290
37. Load Complete #1 OFF
D0301 %DW481
38. 방향 확인 - 입고 '0'
R0010 %RB32
39. JOB NO 기록 (RGV측 위치)
M019.0 %MX304
40. RGV측 Pallet Exist OFF (ID Shift)
M019.1 %MX305
41. S/C측 Pallet Exist ON (도착)
R0012 %RB36
42. PLC ID Shift 결과 : JOB 이 S/C측으로 이동
M018.6 %MX294
43. W.O 보고 (S/C Call)
M019.1 %MX305
44. S/C측 Pallet Exist OFF (S/C Load 완료)
M018.3 %MX291
45. Unload Complete #2 ON (S/C 픽업)
M081.3 %MX1299
46. Unload Complete Ack #2 ON (WCS)
M018.3 %MX291
47. Unload Complete #2 OFF
M018.6 %MX294
48. W.O OFF
④ S/C #1 — 17 스텝
D0160 %DW256
49. IDLE=1 확인
M096.0 %MX1536
50. Transfer Command Req’ (WCS 지시)
D0320 %DW768
51. Transfer Command Data - From (픽업 포트)
D0323 %DW771
52. Transfer Command Data - To (랙 셀(열/연/단))
D0326 %DW774
53. Transfer Command Data - Job No
M048.0 %MX768
54. Pallet Presence ON (S/C 적재)
R0300 %RB1536
55. On S/C - 탑재 화물번호
M049.0 %MX784
56. Load Complete ON
M096.1 %MX1537
57. Load Complete Ack ON (WCS)
D0166 %DW262
58. S/C 현재위치(열/연/단)
M049.0 %MX784
59. Load Complete OFF
M048.0 %MX768
60. Pallet Presence OFF (랙 적치 완료)
M049.1 %MX785
61. Unload Complete ON
M096.2 %MX1538
62. Unload Complete Ack ON (WCS)
D0163 %DW259
63. Transfer Complete Location
M049.1 %MX785
64. Unload Complete OFF
D0160 %DW256
65. IDLE 복귀

## 출고 SC #1 => TR #29
S/C #1 → 피킹대 #29(CV#14) 출고 작업
■ | 노란색 표시: 트랙번호와 실제 포트/슬롯 번호가 다른 주의 지점 — ① C/V#15 역순 슬롯(#30=_03) ② RGV To는 RGV측 포트 지정(도착 트랙 아님) ③ C/V#11 출고모드 전환 구간
# | 구간 | 주체 | 신호 / 설명 | 1호기 | 2호기 | 3호기 | 4호기 | 5호기 | 시스템 | 파일 | 함수
1 | SC 반송 | WCS 값 | IDLE=1 확인 | S/C #1 D0160 %DW256 | S/C #2 D0170 %DW272 | S/C #3 D0180 %DW288 | S/C #4 D0190 %DW304 | S/C #5 D0200 %DW320 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() PollObservations()
2 |  | WCS BIT ON | Transfer Command Req’ (WCS 지시) | S/C #1 M096.0 %MX1536 | S/C #2 M097.0 %MX1552 | S/C #3 M098.0 %MX1568 | S/C #4 M099.0 %MX1584 | S/C #5 M100.0 %MX1600 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() → UpdateScData() ConsumeCommands()
3 |  | WCS 값 | Transfer Command Data - From (랙 셀) | S/C #1 D0320 %DW768 | S/C #2 D0330 %DW784 | S/C #3 D0340 %DW800 | S/C #4 D0350 %DW816 | S/C #5 D0360 %DW832 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() → UpdateScData() ConsumeCommands()
4 |  | WCS 값 | Transfer Command Data - To (하역 포트) | S/C #1 D0323 %DW771 | S/C #2 D0333 %DW787 | S/C #3 D0343 %DW803 | S/C #4 D0353 %DW819 | S/C #5 D0363 %DW835 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() → UpdateScData() ConsumeCommands()
5 |  | WCS 값 | Transfer Command Data - Job No | S/C #1 D0326 %DW774 | S/C #2 D0336 %DW790 | S/C #3 D0346 %DW806 | S/C #4 D0356 %DW822 | S/C #5 D0366 %DW838 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() → UpdateScData() ConsumeCommands()
6 |  | EQP BIT ON | Pallet Presence ON (S/C 적재) | S/C #1 M048.0 %MX768 | S/C #2 M050.0 %MX800 | S/C #3 M052.0 %MX832 | S/C #4 M054.0 %MX864 | S/C #5 M056.0 %MX896
7 |  | WCS 값 | On S/C - 탑재 화물번호 | S/C #1 R0300 %RB1536 | S/C #2 R0302 %RB1540 | S/C #3 R0304 %RB1544 | S/C #4 R0306 %RB1548 | S/C #5 R0308 %RB1552 | EQP_TASK | VehThread.cs | PollObservations()
8 |  | EQP BIT ON | Load Complete ON | S/C #1 M049.0 %MX784 | S/C #2 M051.0 %MX816 | S/C #3 M053.0 %MX848 | S/C #4 M055.0 %MX880 | S/C #5 M057.0 %MX912
9 |  | WCS BIT ON | Load Complete Ack ON (WCS) | S/C #1 M096.1 %MX1537 | S/C #2 M097.1 %MX1553 | S/C #3 M098.1 %MX1569 | S/C #4 M099.1 %MX1585 | S/C #5 M100.1 %MX1601 | EQP_TASK | VehThread.cs | PollObservations()
10 |  | WCS 값 | S/C 현재위치(열/연/단) | S/C #1 D0166 %DW262 | S/C #2 D0176 %DW278 | S/C #3 D0186 %DW294 | S/C #4 D0196 %DW310 | S/C #5 D0206 %DW326 | EQP_TASK | VehThread.cs | PollObservations()
11 |  | EQP BIT OFF | Load Complete OFF | S/C #1 M049.0 %MX784 | S/C #2 M051.0 %MX816 | S/C #3 M053.0 %MX848 | S/C #4 M055.0 %MX880 | S/C #5 M057.0 %MX912
12 |  | EQP BIT OFF | Pallet Presence OFF (통로 C/V 하역 완료) | S/C #1 M048.0 %MX768 | S/C #2 M050.0 %MX800 | S/C #3 M052.0 %MX832 | S/C #4 M054.0 %MX864 | S/C #5 M056.0 %MX896
13 |  | EQP BIT ON | Unload Complete ON | S/C #1 M049.1 %MX785 | S/C #2 M051.1 %MX817 | S/C #3 M053.1 %MX849 | S/C #4 M055.1 %MX881 | S/C #5 M057.1 %MX913
14 |  | WCS BIT ON | Unload Complete Ack ON (WCS) | S/C #1 M096.2 %MX1538 | S/C #2 M097.2 %MX1554 | S/C #3 M098.2 %MX1570 | S/C #4 M099.2 %MX1586 | S/C #5 M100.2 %MX1602 | EQP_TASK | VehThread.cs | PollObservations()
15 |  | WCS 값 | Transfer Complete Location | S/C #1 D0163 %DW259 | S/C #2 D0173 %DW275 | S/C #3 D0183 %DW291 | S/C #4 D0193 %DW307 | S/C #5 D0203 %DW323 | EQP_TASK IO_TASK | VehThread.cs cThread_SCH.cs | PollObservations() CompleteSC()
16 |  | EQP BIT OFF | Unload Complete OFF | S/C #1 M049.1 %MX785 | S/C #2 M051.1 %MX817 | S/C #3 M053.1 %MX849 | S/C #4 M055.1 %MX881 | S/C #5 M057.1 %MX913
17 |  | WCS 값 | IDLE 복귀 | S/C #1 D0160 %DW256 | S/C #2 D0170 %DW272 | S/C #3 D0180 %DW288 | S/C #4 D0190 %DW304 | S/C #5 D0200 %DW320 | EQP_TASK IO_TASK | VehThread.cs cThread_SCH.cs | PollObservations() CompleteSC()
18 | 통로 CV (CV #2, CV #3, CV #5, CV #7, CV #9) | EQP BIT ON | S/C측 Pallet Exist ON (S/C 하역 완료) | C/V #2 M019.1 %MX305 | C/V #3 M021.1 %MX337 | C/V #5 M025.1 %MX401 | C/V #7 M029.1 %MX465 | C/V #9 M033.1 %MX529
19 |  | EQP BIT ON | Load Complete #2 ON | C/V #2 M018.4 %MX292 | C/V #3 M020.4 %MX324 | C/V #5 M024.4 %MX388 | C/V #7 M028.4 %MX452 | C/V #9 M032.4 %MX516
20 |  | WCS BIT ON | Load Complete Ack #2 ON (WCS) | C/V #2 M081.4 %MX1300 | C/V #3 M082.4 %MX1316 | C/V #5 M084.4 %MX1348 | C/V #7 M086.4 %MX1380 | C/V #9 M088.4 %MX1412 | EQP_TASK | CvThread.cs | CvEventCheck()
21 |  | EQP BIT OFF | Load Complete #2 OFF | C/V #2 M018.4 %MX292 | C/V #3 M020.4 %MX324 | C/V #5 M024.4 %MX388 | C/V #7 M028.4 %MX452 | C/V #9 M032.4 %MX516
22 |  | WCS 값 | 방향 확인 - 출고 '1' | C/V #2 D0301 %DW481 | C/V #3 D0302 %DW482 | C/V #5 D0304 %DW484 | C/V #7 D0306 %DW486 | C/V #9 D0308 %DW488 | EQP_TASK IO_TASK | CvThread.cs cThread_SCH.cs | CvStatusScenario() RequestCvDirection()
23 |  | WCS 값 | JOB NO 기록 (S/C측 위치) | C/V #2 R0012 %RB36 | C/V #3 R0022 %RB68 | C/V #5 R0042 %RB132 | C/V #7 R0062 %RB196 | C/V #9 R0082 %RB260 | EQP_TASK IO_TASK | CvThread.cs cThread_SCH.cs | CvTrackingWrite() DriveCV() → UpdateCvData()
24 |  | EQP BIT OFF | S/C측 Pallet Exist OFF (ID Shift) | C/V #2 M019.1 %MX305 | C/V #3 M021.1 %MX337 | C/V #5 M025.1 %MX401 | C/V #7 M029.1 %MX465 | C/V #9 M033.1 %MX529
25 |  | EQP BIT ON | RGV측 Pallet Exist ON (도착) | C/V #2 M019.0 %MX304 | C/V #3 M021.0 %MX336 | C/V #5 M025.0 %MX400 | C/V #7 M029.0 %MX464 | C/V #9 M033.0 %MX528
26 |  | WCS 값 | PLC ID Shift 결과 : JOB 이 RGV측으로 이동 | C/V #2 R0010 %RB32 | C/V #3 R0020 %RB64 | C/V #5 R0040 %RB128 | C/V #7 R0060 %RB192 | C/V #9 R0080 %RB256 | EQP_TASK | CvThread.cs | CvStatusScenario()
27 |  | EQP BIT ON | W.O 보고 (RGV Call) | C/V #2 M018.6 %MX294 | C/V #3 M020.6 %MX326 | C/V #5 M024.6 %MX390 | C/V #7 M028.6 %MX454 | C/V #9 M032.6 %MX518
28 |  | EQP BIT OFF | RGV측 Pallet Exist OFF (RGV Load 완료) | C/V #2 M019.0 %MX304 | C/V #3 M021.0 %MX336 | C/V #5 M025.0 %MX400 | C/V #7 M029.0 %MX464 | C/V #9 M033.0 %MX528
29 |  | EQP BIT ON | Unload Complete #1 ON (RGV 픽업) | C/V #2 M018.1 %MX289 | C/V #3 M020.1 %MX321 | C/V #5 M024.1 %MX385 | C/V #7 M028.1 %MX449 | C/V #9 M032.1 %MX513
30 |  | WCS BIT ON | Unload Complete Ack #1 ON (WCS) | C/V #2 M081.1 %MX1297 | C/V #3 M082.1 %MX1313 | C/V #5 M084.1 %MX1345 | C/V #7 M086.1 %MX1377 | C/V #9 M088.1 %MX1409 | EQP_TASK | CvThread.cs | CvEventCheck()
31 |  | EQP BIT OFF | Unload Complete #1 OFF | C/V #2 M018.1 %MX289 | C/V #3 M020.1 %MX321 | C/V #5 M024.1 %MX385 | C/V #7 M028.1 %MX449 | C/V #9 M032.1 %MX513
32 |  | EQP BIT OFF | W.O OFF | C/V #2 M018.6 %MX294 | C/V #3 M020.6 %MX326 | C/V #5 M024.6 %MX390 | C/V #7 M028.6 %MX454 | C/V #9 M032.6 %MX518
33 | RGV #1 | WCS 값 | IDLE=1 확인 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() PollObservations()
34 |  | WCS BIT ON | Transfer Command Req’ (WCS 지시) | RGV #1 M101.0 %MX1616 | RGV #1 M101.0 %MX1616 | RGV #1 M101.0 %MX1616 | RGV #1 M101.0 %MX1616 | RGV #1 M101.0 %MX1616 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() → UpdateRtvData() ConsumeCommands()
35 |  | WCS 값 | Transfer Command Data - From (픽업 포트) | RGV #1 D0370 %DW848 | RGV #1 D0370 %DW848 | RGV #1 D0370 %DW848 | RGV #1 D0370 %DW848 | RGV #1 D0370 %DW848 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() → UpdateRtvData() ConsumeCommands()
36 |  | WCS 값 | Transfer Command Data - To (29 피킹대 #27) | RGV #1 D0373 %DW851 | RGV #1 D0373 %DW851 | RGV #1 D0373 %DW851 | RGV #1 D0373 %DW851 | RGV #1 D0373 %DW851 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() → UpdateRtvData() ConsumeCommands()
37 |  | WCS 값 | Transfer Command Data - Job No | RGV #1 D0376 %DW854 | RGV #1 D0376 %DW854 | RGV #1 D0376 %DW854 | RGV #1 D0376 %DW854 | RGV #1 D0376 %DW854 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() → UpdateRtvData() ConsumeCommands()
38 |  | EQP BIT ON | Pallet Presence ON (RGV 적재) | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928
39 |  | WCS 값 | On RGV - 탑재 화물번호 | RGV #1 R0310 %RB1568 | RGV #1 R0310 %RB1568 | RGV #1 R0310 %RB1568 | RGV #1 R0310 %RB1568 | RGV #1 R0310 %RB1568 | EQP_TASK | VehThread.cs | PollObservations()
40 |  | EQP BIT ON | Load Complete ON | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944
41 |  | WCS BIT ON | Load Complete Ack ON (WCS) | RGV #1 M101.1 %MX1617 | RGV #1 M101.1 %MX1617 | RGV #1 M101.1 %MX1617 | RGV #1 M101.1 %MX1617 | RGV #1 M101.1 %MX1617 | EQP_TASK | VehThread.cs | PollObservations()
42 |  | WCS 값 | Transfer Complete Location | RGV #1 D0213 %DW339 | RGV #1 D0213 %DW339 | RGV #1 D0213 %DW339 | RGV #1 D0213 %DW339 | RGV #1 D0213 %DW339 | EQP_TASK IO_TASK | VehThread.cs cThread_SCH.cs | PollObservations() CompleteRGV()
43 |  | EQP BIT OFF | Load Complete OFF | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944
44 |  | EQP BIT OFF | Pallet Presence OFF (하역) | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928
45 |  | EQP BIT ON | Unload Complete ON | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945
46 |  | WCS BIT ON | Unload Complete Ack ON (WCS) | RGV #1 M101.2 %MX1618 | RGV #1 M101.2 %MX1618 | RGV #1 M101.2 %MX1618 | RGV #1 M101.2 %MX1618 | RGV #1 M101.2 %MX1618 | EQP_TASK | VehThread.cs | PollObservations()
47 |  | EQP BIT OFF | Unload Complete OFF | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945
48 |  | WCS 값 | IDLE 복귀 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | EQP_TASK IO_TASK | VehThread.cs cThread_SCH.cs | PollObservations() CompleteRGV()
49 | CV #14 | EQP BIT ON | 29 피킹대 RGV측 Pallet Exist ON (RGV 하역) | C/V #14 M043.0 %MX688 | C/V #14 M043.0 %MX688 | C/V #14 M043.0 %MX688 | C/V #14 M043.0 %MX688 | C/V #14 M043.0 %MX688
50 |  | EQP BIT ON | Load Complete #1 ON | C/V #14 M042.2 %MX674 | C/V #14 M042.2 %MX674 | C/V #14 M042.2 %MX674 | C/V #14 M042.2 %MX674 | C/V #14 M042.2 %MX674
51 |  | WCS BIT ON | Load Complete Ack #1 ON (WCS) | C/V #14 M093.2 %MX1490 | C/V #14 M093.2 %MX1490 | C/V #14 M093.2 %MX1490 | C/V #14 M093.2 %MX1490 | C/V #14 M093.2 %MX1490 | EQP_TASK | CvThread.cs | CvEventCheck()
52 |  | EQP BIT OFF | Load Complete #1 OFF | C/V #14 M042.2 %MX674 | C/V #14 M042.2 %MX674 | C/V #14 M042.2 %MX674 | C/V #14 M042.2 %MX674 | C/V #14 M042.2 %MX674
53 |  | WCS 값 | 방향 확인 - 출고 '1' | C/V #14 D0313 %DW493 | C/V #14 D0313 %DW493 | C/V #14 D0313 %DW493 | C/V #14 D0313 %DW493 | C/V #14 D0313 %DW493 | EQP_TASK IO_TASK | CvThread.cs cThread_SCH.cs | CvStatusScenario() RequestCvDirection()
54 |  | WCS 값 | JOB NO 기록 (RGV측 위치) | C/V #14 R0130 %RB608 | C/V #14 R0130 %RB608 | C/V #14 R0130 %RB608 | C/V #14 R0130 %RB608 | C/V #14 R0130 %RB608 | EQP_TASK IO_TASK | CvThread.cs cThread_SCH.cs | CvTrackingWrite() DriveCV() → UpdateCvData()
55 |  | EQP BIT OFF | RGV측 Pallet Exist OFF (ID Shift) | C/V #14 M043.0 %MX688 | C/V #14 M043.0 %MX688 | C/V #14 M043.0 %MX688 | C/V #14 M043.0 %MX688 | C/V #14 M043.0 %MX688
56 |  | EQP BIT ON | 29 피킹대 반출 위치 Pallet Exist ON (도착) | C/V #14 M043.1 %MX689 | C/V #14 M043.1 %MX689 | C/V #14 M043.1 %MX689 | C/V #14 M043.1 %MX689 | C/V #14 M043.1 %MX689
57 |  | WCS 값 | PLC ID Shift 결과 : JOB 이 반출 위치로 이동 | C/V #14 R0132 %RB612 | C/V #14 R0132 %RB612 | C/V #14 R0132 %RB612 | C/V #14 R0132 %RB612 | C/V #14 R0132 %RB612 | EQP_TASK | CvThread.cs | CvStatusScenario()
58 |  | EQP BIT OFF | 29 피킹대 반출 완료 (작업자 회수) | C/V #14 M043.1 %MX689 | C/V #14 M043.1 %MX689 | C/V #14 M043.1 %MX689 | C/V #14 M043.1 %MX689 | C/V #14 M043.1 %MX689 | IO_TASK HOST_TASK | cThread_SCH.cs CCliWork.cs | CompleteCV() GetJobCompleteReport()
반송 시나리오 4-2. S/C → 29 피킹대 출고 (랙 → S/C → 통로 → RGV → C/V #14)
실선 → 비트 ON/OFF · 점선 → D/R 워드 값 기록·확인 · 왼쪽 끝 = M/D/R 영역 문서표기 + 실제 접근주소 (S/C #1 기준)
EQP (설비 / PLC)
ECS (WCS)
① S/C #1 — 17 스텝
D0160 %DW256
1. IDLE=1 확인
M096.0 %MX1536
2. Transfer Command Req’ (WCS 지시)
D0320 %DW768
3. Transfer Command Data - From (랙 셀)
D0323 %DW771
4. Transfer Command Data - To (하역 포트)
D0326 %DW774
5. Transfer Command Data - Job No
M048.0 %MX768
6. Pallet Presence ON (S/C 적재)
R0300 %RB1536
7. On S/C - 탑재 화물번호
M049.0 %MX784
8. Load Complete ON
M096.1 %MX1537
9. Load Complete Ack ON (WCS)
D0166 %DW262
10. S/C 현재위치(열/연/단)
M049.0 %MX784
11. Load Complete OFF
M048.0 %MX768
12. Pallet Presence OFF (통로 C/V 하역 완료)
M049.1 %MX785
13. Unload Complete ON
M096.2 %MX1538
14. Unload Complete Ack ON (WCS)
D0163 %DW259
15. Transfer Complete Location
M049.1 %MX785
16. Unload Complete OFF
D0160 %DW256
17. IDLE 복귀
② C/V #2 — 15 스텝
M019.1 %MX305
18. S/C측 Pallet Exist ON (S/C 하역 완료)
M018.4 %MX292
19. Load Complete #2 ON
M081.4 %MX1300
20. Load Complete Ack #2 ON (WCS)
M018.4 %MX292
21. Load Complete #2 OFF
D0301 %DW481
22. 방향 확인 - 출고 '1'
R0012 %RB36
23. JOB NO 기록 (S/C측 위치)
M019.1 %MX305
24. S/C측 Pallet Exist OFF (ID Shift)
M019.0 %MX304
25. RGV측 Pallet Exist ON (도착)
R0010 %RB32
26. PLC ID Shift 결과 : JOB 이 RGV측으로 이동
M018.6 %MX294
27. W.O 보고 (RGV Call)
M019.0 %MX304
28. RGV측 Pallet Exist OFF (RGV Load 완료)
M018.1 %MX289
29. Unload Complete #1 ON (RGV 픽업)
M081.1 %MX1297
30. Unload Complete Ack #1 ON (WCS)
M018.1 %MX289
31. Unload Complete #1 OFF
M018.6 %MX294
32. W.O OFF
③ RGV #1 — 16 스텝
D0210 %DW336
33. IDLE=1 확인
M101.0 %MX1616
34. Transfer Command Req’ (WCS 지시)
D0370 %DW848
35. Transfer Command Data - From (픽업 포트)
D0373 %DW851
36. Transfer Command Data - To (29 피킹대 #27)
D0376 %DW854
37. Transfer Command Data - Job No
M058.0 %MX928
38. Pallet Presence ON (RGV 적재)
R0310 %RB1568
39. On RGV - 탑재 화물번호
M059.0 %MX944
40. Load Complete ON
M101.1 %MX1617
41. Load Complete Ack ON (WCS)
D0213 %DW339
42. Transfer Complete Location
M059.0 %MX944
43. Load Complete OFF
M058.0 %MX928
44. Pallet Presence OFF (하역)
M059.1 %MX945
45. Unload Complete ON
M101.2 %MX1618
46. Unload Complete Ack ON (WCS)
M059.1 %MX945
47. Unload Complete OFF
D0210 %DW336
48. IDLE 복귀
④ C/V #14 — 10 스텝
M043.0 %MX688
49. 29 피킹대 RGV측 Pallet Exist ON (RGV 하역)
M042.2 %MX674
50. Load Complete #1 ON
M093.2 %MX1490
51. Load Complete Ack #1 ON (WCS)
M042.2 %MX674
52. Load Complete #1 OFF
D0313 %DW493
53. 방향 확인 - 출고 '1'
R0130 %RB608
54. JOB NO 기록 (RGV측 위치)
M043.0 %MX688
55. RGV측 Pallet Exist OFF (ID Shift)
M043.1 %MX689
56. 29 피킹대 반출 위치 Pallet Exist ON (도착)
R0132 %RB612
57. PLC ID Shift 결과 : JOB 이 반출 위치로 이동
M043.1 %MX689
58. 29 피킹대 반출 완료 (작업자 회수)

## 출고 SC #1 => TR #26
S/C #1 → 출고대 #26(CV#13) 출고 작업
■ | 노란색 표시: 트랙번호와 실제 포트/슬롯 번호가 다른 주의 지점 — ① C/V#15 역순 슬롯(#30=_03) ② RGV To는 RGV측 포트 지정(도착 트랙 아님) ③ C/V#11 출고모드 전환 구간
# | 구간 | 주체 | 신호 / 설명 | 1호기 | 2호기 | 3호기 | 4호기 | 5호기 | 시스템 | 파일 | 함수
1 | SC 반송 | WCS 값 | IDLE=1 확인 | S/C #1 D0160 %DW256 | S/C #2 D0170 %DW272 | S/C #3 D0180 %DW288 | S/C #4 D0190 %DW304 | S/C #5 D0200 %DW320 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() PollObservations()
2 |  | WCS BIT ON | Transfer Command Req’ (WCS 지시) | S/C #1 M096.0 %MX1536 | S/C #2 M097.0 %MX1552 | S/C #3 M098.0 %MX1568 | S/C #4 M099.0 %MX1584 | S/C #5 M100.0 %MX1600 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() → UpdateScData() ConsumeCommands()
3 |  | WCS 값 | Transfer Command Data - From (랙 셀) | S/C #1 D0320 %DW768 | S/C #2 D0330 %DW784 | S/C #3 D0340 %DW800 | S/C #4 D0350 %DW816 | S/C #5 D0360 %DW832 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() → UpdateScData() ConsumeCommands()
4 |  | WCS 값 | Transfer Command Data - To (하역 포트) | S/C #1 D0323 %DW771 | S/C #2 D0333 %DW787 | S/C #3 D0343 %DW803 | S/C #4 D0353 %DW819 | S/C #5 D0363 %DW835 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() → UpdateScData() ConsumeCommands()
5 |  | WCS 값 | Transfer Command Data - Job No | S/C #1 D0326 %DW774 | S/C #2 D0336 %DW790 | S/C #3 D0346 %DW806 | S/C #4 D0356 %DW822 | S/C #5 D0366 %DW838 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() → UpdateScData() ConsumeCommands()
6 |  | EQP BIT ON | Pallet Presence ON (S/C 적재) | S/C #1 M048.0 %MX768 | S/C #2 M050.0 %MX800 | S/C #3 M052.0 %MX832 | S/C #4 M054.0 %MX864 | S/C #5 M056.0 %MX896
7 |  | WCS 값 | On S/C - 탑재 화물번호 | S/C #1 R0300 %RB1536 | S/C #2 R0302 %RB1540 | S/C #3 R0304 %RB1544 | S/C #4 R0306 %RB1548 | S/C #5 R0308 %RB1552 | EQP_TASK | VehThread.cs | PollObservations()
8 |  | EQP BIT ON | Load Complete ON | S/C #1 M049.0 %MX784 | S/C #2 M051.0 %MX816 | S/C #3 M053.0 %MX848 | S/C #4 M055.0 %MX880 | S/C #5 M057.0 %MX912
9 |  | WCS BIT ON | Load Complete Ack ON (WCS) | S/C #1 M096.1 %MX1537 | S/C #2 M097.1 %MX1553 | S/C #3 M098.1 %MX1569 | S/C #4 M099.1 %MX1585 | S/C #5 M100.1 %MX1601 | EQP_TASK | VehThread.cs | PollObservations()
10 |  | WCS 값 | S/C 현재위치(열/연/단) | S/C #1 D0166 %DW262 | S/C #2 D0176 %DW278 | S/C #3 D0186 %DW294 | S/C #4 D0196 %DW310 | S/C #5 D0206 %DW326 | EQP_TASK | VehThread.cs | PollObservations()
11 |  | EQP BIT OFF | Load Complete OFF | S/C #1 M049.0 %MX784 | S/C #2 M051.0 %MX816 | S/C #3 M053.0 %MX848 | S/C #4 M055.0 %MX880 | S/C #5 M057.0 %MX912
12 |  | EQP BIT OFF | Pallet Presence OFF (통로 C/V 하역 완료) | S/C #1 M048.0 %MX768 | S/C #2 M050.0 %MX800 | S/C #3 M052.0 %MX832 | S/C #4 M054.0 %MX864 | S/C #5 M056.0 %MX896
13 |  | EQP BIT ON | Unload Complete ON | S/C #1 M049.1 %MX785 | S/C #2 M051.1 %MX817 | S/C #3 M053.1 %MX849 | S/C #4 M055.1 %MX881 | S/C #5 M057.1 %MX913
14 |  | WCS BIT ON | Unload Complete Ack ON (WCS) | S/C #1 M096.2 %MX1538 | S/C #2 M097.2 %MX1554 | S/C #3 M098.2 %MX1570 | S/C #4 M099.2 %MX1586 | S/C #5 M100.2 %MX1602 | EQP_TASK | VehThread.cs | PollObservations()
15 |  | WCS 값 | Transfer Complete Location | S/C #1 D0163 %DW259 | S/C #2 D0173 %DW275 | S/C #3 D0183 %DW291 | S/C #4 D0193 %DW307 | S/C #5 D0203 %DW323 | EQP_TASK IO_TASK | VehThread.cs cThread_SCH.cs | PollObservations() CompleteSC()
16 |  | EQP BIT OFF | Unload Complete OFF | S/C #1 M049.1 %MX785 | S/C #2 M051.1 %MX817 | S/C #3 M053.1 %MX849 | S/C #4 M055.1 %MX881 | S/C #5 M057.1 %MX913
17 |  | WCS 값 | IDLE 복귀 | S/C #1 D0160 %DW256 | S/C #2 D0170 %DW272 | S/C #3 D0180 %DW288 | S/C #4 D0190 %DW304 | S/C #5 D0200 %DW320 | EQP_TASK IO_TASK | VehThread.cs cThread_SCH.cs | PollObservations() CompleteSC()
18 | 통로 CV (CV #2, CV #3, CV #5, CV #7, CV #9) | EQP BIT ON | S/C측 Pallet Exist ON (S/C 하역 완료) | C/V #2 M019.1 %MX305 | C/V #3 M021.1 %MX337 | C/V #5 M025.1 %MX401 | C/V #7 M029.1 %MX465 | C/V #9 M033.1 %MX529
19 |  | EQP BIT ON | Load Complete #2 ON | C/V #2 M018.4 %MX292 | C/V #3 M020.4 %MX324 | C/V #5 M024.4 %MX388 | C/V #7 M028.4 %MX452 | C/V #9 M032.4 %MX516
20 |  | WCS BIT ON | Load Complete Ack #2 ON (WCS) | C/V #2 M081.4 %MX1300 | C/V #3 M082.4 %MX1316 | C/V #5 M084.4 %MX1348 | C/V #7 M086.4 %MX1380 | C/V #9 M088.4 %MX1412 | EQP_TASK | CvThread.cs | CvEventCheck()
21 |  | EQP BIT OFF | Load Complete #2 OFF | C/V #2 M018.4 %MX292 | C/V #3 M020.4 %MX324 | C/V #5 M024.4 %MX388 | C/V #7 M028.4 %MX452 | C/V #9 M032.4 %MX516
22 |  | WCS 값 | 방향 확인 - 출고 '1' | C/V #2 D0301 %DW481 | C/V #3 D0302 %DW482 | C/V #5 D0304 %DW484 | C/V #7 D0306 %DW486 | C/V #9 D0308 %DW488 | EQP_TASK IO_TASK | CvThread.cs cThread_SCH.cs | CvStatusScenario() RequestCvDirection()
23 |  | WCS 값 | JOB NO 기록 (S/C측 위치) | C/V #2 R0012 %RB36 | C/V #3 R0022 %RB68 | C/V #5 R0042 %RB132 | C/V #7 R0062 %RB196 | C/V #9 R0082 %RB260 | EQP_TASK IO_TASK | CvThread.cs cThread_SCH.cs | CvTrackingWrite() DriveCV() → UpdateCvData()
24 |  | EQP BIT OFF | S/C측 Pallet Exist OFF (ID Shift) | C/V #2 M019.1 %MX305 | C/V #3 M021.1 %MX337 | C/V #5 M025.1 %MX401 | C/V #7 M029.1 %MX465 | C/V #9 M033.1 %MX529
25 |  | EQP BIT ON | RGV측 Pallet Exist ON (도착) | C/V #2 M019.0 %MX304 | C/V #3 M021.0 %MX336 | C/V #5 M025.0 %MX400 | C/V #7 M029.0 %MX464 | C/V #9 M033.0 %MX528
26 |  | WCS 값 | PLC ID Shift 결과 : JOB 이 RGV측으로 이동 | C/V #2 R0010 %RB32 | C/V #3 R0020 %RB64 | C/V #5 R0040 %RB128 | C/V #7 R0060 %RB192 | C/V #9 R0080 %RB256 | EQP_TASK | CvThread.cs | CvStatusScenario()
27 |  | EQP BIT ON | W.O 보고 (RGV Call) | C/V #2 M018.6 %MX294 | C/V #3 M020.6 %MX326 | C/V #5 M024.6 %MX390 | C/V #7 M028.6 %MX454 | C/V #9 M032.6 %MX518
28 |  | EQP BIT OFF | RGV측 Pallet Exist OFF (RGV Load 완료) | C/V #2 M019.0 %MX304 | C/V #3 M021.0 %MX336 | C/V #5 M025.0 %MX400 | C/V #7 M029.0 %MX464 | C/V #9 M033.0 %MX528
29 |  | EQP BIT ON | Unload Complete #1 ON (RGV 픽업) | C/V #2 M018.1 %MX289 | C/V #3 M020.1 %MX321 | C/V #5 M024.1 %MX385 | C/V #7 M028.1 %MX449 | C/V #9 M032.1 %MX513
30 |  | WCS BIT ON | Unload Complete Ack #1 ON (WCS) | C/V #2 M081.1 %MX1297 | C/V #3 M082.1 %MX1313 | C/V #5 M084.1 %MX1345 | C/V #7 M086.1 %MX1377 | C/V #9 M088.1 %MX1409 | EQP_TASK | CvThread.cs | CvEventCheck()
31 |  | EQP BIT OFF | Unload Complete #1 OFF | C/V #2 M018.1 %MX289 | C/V #3 M020.1 %MX321 | C/V #5 M024.1 %MX385 | C/V #7 M028.1 %MX449 | C/V #9 M032.1 %MX513
32 |  | EQP BIT OFF | W.O OFF | C/V #2 M018.6 %MX294 | C/V #3 M020.6 %MX326 | C/V #5 M024.6 %MX390 | C/V #7 M028.6 %MX454 | C/V #9 M032.6 %MX518
33 | RGV #1 | WCS 값 | IDLE=1 확인 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() PollObservations()
34 |  | WCS BIT ON | Transfer Command Req’ (WCS 지시) | RGV #1 M101.0 %MX1616 | RGV #1 M101.0 %MX1616 | RGV #1 M101.0 %MX1616 | RGV #1 M101.0 %MX1616 | RGV #1 M101.0 %MX1616 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() → UpdateRtvData() ConsumeCommands()
35 |  | WCS 값 | Transfer Command Data - From (픽업 포트) | RGV #1 D0370 %DW848 | RGV #1 D0370 %DW848 | RGV #1 D0370 %DW848 | RGV #1 D0370 %DW848 | RGV #1 D0370 %DW848 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() → UpdateRtvData() ConsumeCommands()
36 |  | WCS 값 | Transfer Command Data - To (26 출고대 #25) | RGV #1 D0373 %DW851 | RGV #1 D0373 %DW851 | RGV #1 D0373 %DW851 | RGV #1 D0373 %DW851 | RGV #1 D0373 %DW851 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() → UpdateRtvData() ConsumeCommands()
37 |  | WCS 값 | Transfer Command Data - Job No | RGV #1 D0376 %DW854 | RGV #1 D0376 %DW854 | RGV #1 D0376 %DW854 | RGV #1 D0376 %DW854 | RGV #1 D0376 %DW854 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() → UpdateRtvData() ConsumeCommands()
38 |  | EQP BIT ON | Pallet Presence ON (RGV 적재) | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928
39 |  | WCS 값 | On RGV - 탑재 화물번호 | RGV #1 R0310 %RB1568 | RGV #1 R0310 %RB1568 | RGV #1 R0310 %RB1568 | RGV #1 R0310 %RB1568 | RGV #1 R0310 %RB1568 | EQP_TASK | VehThread.cs | PollObservations()
40 |  | EQP BIT ON | Load Complete ON | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944
41 |  | WCS BIT ON | Load Complete Ack ON (WCS) | RGV #1 M101.1 %MX1617 | RGV #1 M101.1 %MX1617 | RGV #1 M101.1 %MX1617 | RGV #1 M101.1 %MX1617 | RGV #1 M101.1 %MX1617 | EQP_TASK | VehThread.cs | PollObservations()
42 |  | WCS 값 | Transfer Complete Location | RGV #1 D0213 %DW339 | RGV #1 D0213 %DW339 | RGV #1 D0213 %DW339 | RGV #1 D0213 %DW339 | RGV #1 D0213 %DW339 | EQP_TASK IO_TASK | VehThread.cs cThread_SCH.cs | PollObservations() CompleteRGV()
43 |  | EQP BIT OFF | Load Complete OFF | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944
44 |  | EQP BIT OFF | Pallet Presence OFF (하역) | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928
45 |  | EQP BIT ON | Unload Complete ON | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945
46 |  | WCS BIT ON | Unload Complete Ack ON (WCS) | RGV #1 M101.2 %MX1618 | RGV #1 M101.2 %MX1618 | RGV #1 M101.2 %MX1618 | RGV #1 M101.2 %MX1618 | RGV #1 M101.2 %MX1618 | EQP_TASK | VehThread.cs | PollObservations()
47 |  | EQP BIT OFF | Unload Complete OFF | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945
48 |  | WCS 값 | IDLE 복귀 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | EQP_TASK IO_TASK | VehThread.cs cThread_SCH.cs | PollObservations() CompleteRGV()
49 | CV #13 | EQP BIT ON | 26 출고대 RGV측 Pallet Exist ON (RGV 하역) | C/V #13 M041.0 %MX656 | C/V #13 M041.0 %MX656 | C/V #13 M041.0 %MX656 | C/V #13 M041.0 %MX656 | C/V #13 M041.0 %MX656
50 |  | EQP BIT ON | Load Complete #1 ON | C/V #13 M040.2 %MX642 | C/V #13 M040.2 %MX642 | C/V #13 M040.2 %MX642 | C/V #13 M040.2 %MX642 | C/V #13 M040.2 %MX642
51 |  | WCS BIT ON | Load Complete Ack #1 ON (WCS) | C/V #13 M092.2 %MX1474 | C/V #13 M092.2 %MX1474 | C/V #13 M092.2 %MX1474 | C/V #13 M092.2 %MX1474 | C/V #13 M092.2 %MX1474 | EQP_TASK | CvThread.cs | CvEventCheck()
52 |  | EQP BIT OFF | Load Complete #1 OFF | C/V #13 M040.2 %MX642 | C/V #13 M040.2 %MX642 | C/V #13 M040.2 %MX642 | C/V #13 M040.2 %MX642 | C/V #13 M040.2 %MX642
53 |  | WCS 값 | 방향 확인 - 출고 '1' | C/V #13 D0312 %DW492 | C/V #13 D0312 %DW492 | C/V #13 D0312 %DW492 | C/V #13 D0312 %DW492 | C/V #13 D0312 %DW492 | EQP_TASK IO_TASK | CvThread.cs cThread_SCH.cs | CvStatusScenario() RequestCvDirection()
54 |  | WCS 값 | JOB NO 기록 (RGV측 위치) | C/V #13 R0120 %RB576 | C/V #13 R0120 %RB576 | C/V #13 R0120 %RB576 | C/V #13 R0120 %RB576 | C/V #13 R0120 %RB576 | EQP_TASK IO_TASK | CvThread.cs cThread_SCH.cs | CvTrackingWrite() DriveCV() → UpdateCvData()
55 |  | EQP BIT OFF | RGV측 Pallet Exist OFF (ID Shift) | C/V #13 M041.0 %MX656 | C/V #13 M041.0 %MX656 | C/V #13 M041.0 %MX656 | C/V #13 M041.0 %MX656 | C/V #13 M041.0 %MX656
56 |  | EQP BIT ON | 26 출고대 반출 위치 Pallet Exist ON (도착) | C/V #13 M041.1 %MX657 | C/V #13 M041.1 %MX657 | C/V #13 M041.1 %MX657 | C/V #13 M041.1 %MX657 | C/V #13 M041.1 %MX657
57 |  | WCS 값 | PLC ID Shift 결과 : JOB 이 반출 위치로 이동 | C/V #13 R0122 %RB580 | C/V #13 R0122 %RB580 | C/V #13 R0122 %RB580 | C/V #13 R0122 %RB580 | C/V #13 R0122 %RB580 | EQP_TASK | CvThread.cs | CvStatusScenario()
58 |  | EQP BIT OFF | 26 출고대 반출 완료 (작업자 회수) | C/V #13 M041.1 %MX657 | C/V #13 M041.1 %MX657 | C/V #13 M041.1 %MX657 | C/V #13 M041.1 %MX657 | C/V #13 M041.1 %MX657 | IO_TASK HOST_TASK | cThread_SCH.cs CCliWork.cs | CompleteCV() GetJobCompleteReport()
반송 시나리오 3-2. S/C → 26 출고대 출고 (랙 → S/C → 통로 → RGV → C/V #13)
실선 → 비트 ON/OFF · 점선 → D/R 워드 값 기록·확인 · 왼쪽 끝 = M/D/R 영역 문서표기 + 실제 접근주소 (S/C #1 기준)
EQP (설비 / PLC)
ECS (WCS)
① S/C #1 — 17 스텝
D0160 %DW256
1. IDLE=1 확인
M096.0 %MX1536
2. Transfer Command Req’ (WCS 지시)
D0320 %DW768
3. Transfer Command Data - From (랙 셀)
D0323 %DW771
4. Transfer Command Data - To (하역 포트)
D0326 %DW774
5. Transfer Command Data - Job No
M048.0 %MX768
6. Pallet Presence ON (S/C 적재)
R0300 %RB1536
7. On S/C - 탑재 화물번호
M049.0 %MX784
8. Load Complete ON
M096.1 %MX1537
9. Load Complete Ack ON (WCS)
D0166 %DW262
10. S/C 현재위치(열/연/단)
M049.0 %MX784
11. Load Complete OFF
M048.0 %MX768
12. Pallet Presence OFF (통로 C/V 하역 완료)
M049.1 %MX785
13. Unload Complete ON
M096.2 %MX1538
14. Unload Complete Ack ON (WCS)
D0163 %DW259
15. Transfer Complete Location
M049.1 %MX785
16. Unload Complete OFF
D0160 %DW256
17. IDLE 복귀
② C/V #2 — 15 스텝
M019.1 %MX305
18. S/C측 Pallet Exist ON (S/C 하역 완료)
M018.4 %MX292
19. Load Complete #2 ON
M081.4 %MX1300
20. Load Complete Ack #2 ON (WCS)
M018.4 %MX292
21. Load Complete #2 OFF
D0301 %DW481
22. 방향 확인 - 출고 '1'
R0012 %RB36
23. JOB NO 기록 (S/C측 위치)
M019.1 %MX305
24. S/C측 Pallet Exist OFF (ID Shift)
M019.0 %MX304
25. RGV측 Pallet Exist ON (도착)
R0010 %RB32
26. PLC ID Shift 결과 : JOB 이 RGV측으로 이동
M018.6 %MX294
27. W.O 보고 (RGV Call)
M019.0 %MX304
28. RGV측 Pallet Exist OFF (RGV Load 완료)
M018.1 %MX289
29. Unload Complete #1 ON (RGV 픽업)
M081.1 %MX1297
30. Unload Complete Ack #1 ON (WCS)
M018.1 %MX289
31. Unload Complete #1 OFF
M018.6 %MX294
32. W.O OFF
③ RGV #1 — 16 스텝
D0210 %DW336
33. IDLE=1 확인
M101.0 %MX1616
34. Transfer Command Req’ (WCS 지시)
D0370 %DW848
35. Transfer Command Data - From (픽업 포트)
D0373 %DW851
36. Transfer Command Data - To (26 출고대 #25)
D0376 %DW854
37. Transfer Command Data - Job No
M058.0 %MX928
38. Pallet Presence ON (RGV 적재)
R0310 %RB1568
39. On RGV - 탑재 화물번호
M059.0 %MX944
40. Load Complete ON
M101.1 %MX1617
41. Load Complete Ack ON (WCS)
D0213 %DW339
42. Transfer Complete Location
M059.0 %MX944
43. Load Complete OFF
M058.0 %MX928
44. Pallet Presence OFF (하역)
M059.1 %MX945
45. Unload Complete ON
M101.2 %MX1618
46. Unload Complete Ack ON (WCS)
M059.1 %MX945
47. Unload Complete OFF
D0210 %DW336
48. IDLE 복귀
④ C/V #13 — 10 스텝
M041.0 %MX656
49. 26 출고대 RGV측 Pallet Exist ON (RGV 하역)
M040.2 %MX642
50. Load Complete #1 ON
M092.2 %MX1474
51. Load Complete Ack #1 ON (WCS)
M040.2 %MX642
52. Load Complete #1 OFF
D0312 %DW492
53. 방향 확인 - 출고 '1'
R0120 %RB576
54. JOB NO 기록 (RGV측 위치)
M041.0 %MX656
55. RGV측 Pallet Exist OFF (ID Shift)
M041.1 %MX657
56. 26 출고대 반출 위치 Pallet Exist ON (도착)
R0122 %RB580
57. PLC ID Shift 결과 : JOB 이 반출 위치로 이동
M041.1 %MX657
58. 26 출고대 반출 완료 (작업자 회수)

## 출고 SC #1 => TR #22
S/C #1 → 입출고대 #22(CV#11) 출고 작업
■ | 노란색 표시: 트랙번호와 실제 포트/슬롯 번호가 다른 주의 지점 — ① C/V#15 역순 슬롯(#30=_03) ② RGV To는 RGV측 포트 지정(도착 트랙 아님) ③ C/V#11 출고모드 전환 구간
# | 구간 | 주체 | 신호 / 설명 | 1호기 | 2호기 | 3호기 | 4호기 | 5호기 | 시스템 | 파일 | 함수
1 | SC 반송 | WCS 값 | IDLE=1 확인 | S/C #1 D0160 %DW256 | S/C #2 D0170 %DW272 | S/C #3 D0180 %DW288 | S/C #4 D0190 %DW304 | S/C #5 D0200 %DW320 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() PollObservations()
2 |  | WCS BIT ON | Transfer Command Req’ (WCS 지시) | S/C #1 M096.0 %MX1536 | S/C #2 M097.0 %MX1552 | S/C #3 M098.0 %MX1568 | S/C #4 M099.0 %MX1584 | S/C #5 M100.0 %MX1600 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() → UpdateScData() ConsumeCommands()
3 |  | WCS 값 | Transfer Command Data - From (랙 셀) | S/C #1 D0320 %DW768 | S/C #2 D0330 %DW784 | S/C #3 D0340 %DW800 | S/C #4 D0350 %DW816 | S/C #5 D0360 %DW832 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() → UpdateScData() ConsumeCommands()
4 |  | WCS 값 | Transfer Command Data - To (하역 포트) | S/C #1 D0323 %DW771 | S/C #2 D0333 %DW787 | S/C #3 D0343 %DW803 | S/C #4 D0353 %DW819 | S/C #5 D0363 %DW835 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() → UpdateScData() ConsumeCommands()
5 |  | WCS 값 | Transfer Command Data - Job No | S/C #1 D0326 %DW774 | S/C #2 D0336 %DW790 | S/C #3 D0346 %DW806 | S/C #4 D0356 %DW822 | S/C #5 D0366 %DW838 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveSC() → UpdateScData() ConsumeCommands()
6 |  | EQP BIT ON | Pallet Presence ON (S/C 적재) | S/C #1 M048.0 %MX768 | S/C #2 M050.0 %MX800 | S/C #3 M052.0 %MX832 | S/C #4 M054.0 %MX864 | S/C #5 M056.0 %MX896
7 |  | WCS 값 | On S/C - 탑재 화물번호 | S/C #1 R0300 %RB1536 | S/C #2 R0302 %RB1540 | S/C #3 R0304 %RB1544 | S/C #4 R0306 %RB1548 | S/C #5 R0308 %RB1552 | EQP_TASK | VehThread.cs | PollObservations()
8 |  | EQP BIT ON | Load Complete ON | S/C #1 M049.0 %MX784 | S/C #2 M051.0 %MX816 | S/C #3 M053.0 %MX848 | S/C #4 M055.0 %MX880 | S/C #5 M057.0 %MX912
9 |  | WCS BIT ON | Load Complete Ack ON (WCS) | S/C #1 M096.1 %MX1537 | S/C #2 M097.1 %MX1553 | S/C #3 M098.1 %MX1569 | S/C #4 M099.1 %MX1585 | S/C #5 M100.1 %MX1601 | EQP_TASK | VehThread.cs | PollObservations()
10 |  | WCS 값 | S/C 현재위치(열/연/단) | S/C #1 D0166 %DW262 | S/C #2 D0176 %DW278 | S/C #3 D0186 %DW294 | S/C #4 D0196 %DW310 | S/C #5 D0206 %DW326 | EQP_TASK | VehThread.cs | PollObservations()
11 |  | EQP BIT OFF | Load Complete OFF | S/C #1 M049.0 %MX784 | S/C #2 M051.0 %MX816 | S/C #3 M053.0 %MX848 | S/C #4 M055.0 %MX880 | S/C #5 M057.0 %MX912
12 |  | EQP BIT OFF | Pallet Presence OFF (통로 C/V 하역 완료) | S/C #1 M048.0 %MX768 | S/C #2 M050.0 %MX800 | S/C #3 M052.0 %MX832 | S/C #4 M054.0 %MX864 | S/C #5 M056.0 %MX896
13 |  | EQP BIT ON | Unload Complete ON | S/C #1 M049.1 %MX785 | S/C #2 M051.1 %MX817 | S/C #3 M053.1 %MX849 | S/C #4 M055.1 %MX881 | S/C #5 M057.1 %MX913
14 |  | WCS BIT ON | Unload Complete Ack ON (WCS) | S/C #1 M096.2 %MX1538 | S/C #2 M097.2 %MX1554 | S/C #3 M098.2 %MX1570 | S/C #4 M099.2 %MX1586 | S/C #5 M100.2 %MX1602 | EQP_TASK | VehThread.cs | PollObservations()
15 |  | WCS 값 | Transfer Complete Location | S/C #1 D0163 %DW259 | S/C #2 D0173 %DW275 | S/C #3 D0183 %DW291 | S/C #4 D0193 %DW307 | S/C #5 D0203 %DW323 | EQP_TASK IO_TASK | VehThread.cs cThread_SCH.cs | PollObservations() CompleteSC()
16 |  | EQP BIT OFF | Unload Complete OFF | S/C #1 M049.1 %MX785 | S/C #2 M051.1 %MX817 | S/C #3 M053.1 %MX849 | S/C #4 M055.1 %MX881 | S/C #5 M057.1 %MX913
17 |  | WCS 값 | IDLE 복귀 | S/C #1 D0160 %DW256 | S/C #2 D0170 %DW272 | S/C #3 D0180 %DW288 | S/C #4 D0190 %DW304 | S/C #5 D0200 %DW320 | EQP_TASK IO_TASK | VehThread.cs cThread_SCH.cs | PollObservations() CompleteSC()
18 | 통로 CV (CV #2, CV #3, CV #5, CV #7, CV #9) | EQP BIT ON | S/C측 Pallet Exist ON (S/C 하역 완료) | C/V #2 M019.1 %MX305 | C/V #3 M021.1 %MX337 | C/V #5 M025.1 %MX401 | C/V #7 M029.1 %MX465 | C/V #9 M033.1 %MX529
19 |  | EQP BIT ON | Load Complete #2 ON | C/V #2 M018.4 %MX292 | C/V #3 M020.4 %MX324 | C/V #5 M024.4 %MX388 | C/V #7 M028.4 %MX452 | C/V #9 M032.4 %MX516
20 |  | WCS BIT ON | Load Complete Ack #2 ON (WCS) | C/V #2 M081.4 %MX1300 | C/V #3 M082.4 %MX1316 | C/V #5 M084.4 %MX1348 | C/V #7 M086.4 %MX1380 | C/V #9 M088.4 %MX1412 | EQP_TASK | CvThread.cs | CvEventCheck()
21 |  | EQP BIT OFF | Load Complete #2 OFF | C/V #2 M018.4 %MX292 | C/V #3 M020.4 %MX324 | C/V #5 M024.4 %MX388 | C/V #7 M028.4 %MX452 | C/V #9 M032.4 %MX516
22 |  | WCS 값 | 방향 확인 - 출고 '1' | C/V #2 D0301 %DW481 | C/V #3 D0302 %DW482 | C/V #5 D0304 %DW484 | C/V #7 D0306 %DW486 | C/V #9 D0308 %DW488 | EQP_TASK IO_TASK | CvThread.cs cThread_SCH.cs | CvStatusScenario() RequestCvDirection()
23 |  | WCS 값 | JOB NO 기록 (S/C측 위치) | C/V #2 R0012 %RB36 | C/V #3 R0022 %RB68 | C/V #5 R0042 %RB132 | C/V #7 R0062 %RB196 | C/V #9 R0082 %RB260 | EQP_TASK IO_TASK | CvThread.cs cThread_SCH.cs | CvTrackingWrite() DriveCV() → UpdateCvData()
24 |  | EQP BIT OFF | S/C측 Pallet Exist OFF (ID Shift) | C/V #2 M019.1 %MX305 | C/V #3 M021.1 %MX337 | C/V #5 M025.1 %MX401 | C/V #7 M029.1 %MX465 | C/V #9 M033.1 %MX529
25 |  | EQP BIT ON | RGV측 Pallet Exist ON (도착) | C/V #2 M019.0 %MX304 | C/V #3 M021.0 %MX336 | C/V #5 M025.0 %MX400 | C/V #7 M029.0 %MX464 | C/V #9 M033.0 %MX528
26 |  | WCS 값 | PLC ID Shift 결과 : JOB 이 RGV측으로 이동 | C/V #2 R0010 %RB32 | C/V #3 R0020 %RB64 | C/V #5 R0040 %RB128 | C/V #7 R0060 %RB192 | C/V #9 R0080 %RB256 | EQP_TASK | CvThread.cs | CvStatusScenario()
27 |  | EQP BIT ON | W.O 보고 (RGV Call) | C/V #2 M018.6 %MX294 | C/V #3 M020.6 %MX326 | C/V #5 M024.6 %MX390 | C/V #7 M028.6 %MX454 | C/V #9 M032.6 %MX518
28 |  | EQP BIT OFF | RGV측 Pallet Exist OFF (RGV Load 완료) | C/V #2 M019.0 %MX304 | C/V #3 M021.0 %MX336 | C/V #5 M025.0 %MX400 | C/V #7 M029.0 %MX464 | C/V #9 M033.0 %MX528
29 |  | EQP BIT ON | Unload Complete #1 ON (RGV 픽업) | C/V #2 M018.1 %MX289 | C/V #3 M020.1 %MX321 | C/V #5 M024.1 %MX385 | C/V #7 M028.1 %MX449 | C/V #9 M032.1 %MX513
30 |  | WCS BIT ON | Unload Complete Ack #1 ON (WCS) | C/V #2 M081.1 %MX1297 | C/V #3 M082.1 %MX1313 | C/V #5 M084.1 %MX1345 | C/V #7 M086.1 %MX1377 | C/V #9 M088.1 %MX1409 | EQP_TASK | CvThread.cs | CvEventCheck()
31 |  | EQP BIT OFF | Unload Complete #1 OFF | C/V #2 M018.1 %MX289 | C/V #3 M020.1 %MX321 | C/V #5 M024.1 %MX385 | C/V #7 M028.1 %MX449 | C/V #9 M032.1 %MX513
32 |  | EQP BIT OFF | W.O OFF | C/V #2 M018.6 %MX294 | C/V #3 M020.6 %MX326 | C/V #5 M024.6 %MX390 | C/V #7 M028.6 %MX454 | C/V #9 M032.6 %MX518
33 | RGV #1 | WCS 값 | IDLE=1 확인 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() PollObservations()
34 |  | WCS BIT ON | Transfer Command Req’ (WCS 지시) | RGV #1 M101.0 %MX1616 | RGV #1 M101.0 %MX1616 | RGV #1 M101.0 %MX1616 | RGV #1 M101.0 %MX1616 | RGV #1 M101.0 %MX1616 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() → UpdateRtvData() ConsumeCommands()
35 |  | WCS 값 | Transfer Command Data - From (픽업 포트) | RGV #1 D0370 %DW848 | RGV #1 D0370 %DW848 | RGV #1 D0370 %DW848 | RGV #1 D0370 %DW848 | RGV #1 D0370 %DW848 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() → UpdateRtvData() ConsumeCommands()
36 |  | WCS 값 | Transfer Command Data - To (입출고대 #21) | RGV #1 D0373 %DW851 | RGV #1 D0373 %DW851 | RGV #1 D0373 %DW851 | RGV #1 D0373 %DW851 | RGV #1 D0373 %DW851 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() → UpdateRtvData() ConsumeCommands()
37 |  | WCS 값 | Transfer Command Data - Job No | RGV #1 D0376 %DW854 | RGV #1 D0376 %DW854 | RGV #1 D0376 %DW854 | RGV #1 D0376 %DW854 | RGV #1 D0376 %DW854 | IO_TASK EQP_TASK | cThread_SCH.cs VehThread.cs | DriveRGV() → UpdateRtvData() ConsumeCommands()
38 |  | EQP BIT ON | Pallet Presence ON (RGV 적재) | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928
39 |  | WCS 값 | On RGV - 탑재 화물번호 | RGV #1 R0310 %RB1568 | RGV #1 R0310 %RB1568 | RGV #1 R0310 %RB1568 | RGV #1 R0310 %RB1568 | RGV #1 R0310 %RB1568 | EQP_TASK | VehThread.cs | PollObservations()
40 |  | EQP BIT ON | Load Complete ON | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944
41 |  | WCS BIT ON | Load Complete Ack ON (WCS) | RGV #1 M101.1 %MX1617 | RGV #1 M101.1 %MX1617 | RGV #1 M101.1 %MX1617 | RGV #1 M101.1 %MX1617 | RGV #1 M101.1 %MX1617 | EQP_TASK | VehThread.cs | PollObservations()
42 |  | WCS 값 | Transfer Complete Location | RGV #1 D0213 %DW339 | RGV #1 D0213 %DW339 | RGV #1 D0213 %DW339 | RGV #1 D0213 %DW339 | RGV #1 D0213 %DW339 | EQP_TASK IO_TASK | VehThread.cs cThread_SCH.cs | PollObservations() CompleteRGV()
43 |  | EQP BIT OFF | Load Complete OFF | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944 | RGV #1 M059.0 %MX944
44 |  | EQP BIT OFF | Pallet Presence OFF (하역) | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928 | RGV #1 M058.0 %MX928
45 |  | EQP BIT ON | Unload Complete ON | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945
46 |  | WCS BIT ON | Unload Complete Ack ON (WCS) | RGV #1 M101.2 %MX1618 | RGV #1 M101.2 %MX1618 | RGV #1 M101.2 %MX1618 | RGV #1 M101.2 %MX1618 | RGV #1 M101.2 %MX1618 | EQP_TASK | VehThread.cs | PollObservations()
47 |  | EQP BIT OFF | Unload Complete OFF | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945 | RGV #1 M059.1 %MX945
48 |  | WCS 값 | IDLE 복귀 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | RGV #1 D0210 %DW336 | EQP_TASK IO_TASK | VehThread.cs cThread_SCH.cs | PollObservations() CompleteRGV()
49 | CV #11 | EQP BIT ON | 입출고대 RGV측 Pallet Exist ON (RGV 하역) | C/V #11 M037.0 %MX592 | C/V #11 M037.0 %MX592 | C/V #11 M037.0 %MX592 | C/V #11 M037.0 %MX592 | C/V #11 M037.0 %MX592
50 |  | EQP BIT ON | Load Complete #1 ON | C/V #11 M036.2 %MX578 | C/V #11 M036.2 %MX578 | C/V #11 M036.2 %MX578 | C/V #11 M036.2 %MX578 | C/V #11 M036.2 %MX578
51 |  | WCS BIT ON | Load Complete Ack #1 ON (WCS) | C/V #11 M090.2 %MX1442 | C/V #11 M090.2 %MX1442 | C/V #11 M090.2 %MX1442 | C/V #11 M090.2 %MX1442 | C/V #11 M090.2 %MX1442 | EQP_TASK | CvThread.cs | CvEventCheck()
52 |  | EQP BIT OFF | Load Complete #1 OFF | C/V #11 M036.2 %MX578 | C/V #11 M036.2 %MX578 | C/V #11 M036.2 %MX578 | C/V #11 M036.2 %MX578 | C/V #11 M036.2 %MX578
53 |  | WCS 값 | 방향 확인 - 출고 '1' | C/V #11 D0310 %DW490 | C/V #11 D0310 %DW490 | C/V #11 D0310 %DW490 | C/V #11 D0310 %DW490 | C/V #11 D0310 %DW490 | EQP_TASK IO_TASK | CvThread.cs cThread_SCH.cs | CvStatusScenario() RequestCvDirection()
54 |  | WCS 값 | JOB NO 기록 (RGV측 위치) | C/V #11 R0100 %RB512 | C/V #11 R0100 %RB512 | C/V #11 R0100 %RB512 | C/V #11 R0100 %RB512 | C/V #11 R0100 %RB512 | EQP_TASK IO_TASK | CvThread.cs cThread_SCH.cs | CvTrackingWrite() DriveCV() → UpdateCvData()
55 |  | EQP BIT OFF | RGV측 Pallet Exist OFF (ID Shift) | C/V #11 M037.0 %MX592 | C/V #11 M037.0 %MX592 | C/V #11 M037.0 %MX592 | C/V #11 M037.0 %MX592 | C/V #11 M037.0 %MX592
56 |  | EQP BIT ON | 입출고대 반출 위치 Pallet Exist ON (도착) | C/V #11 M037.1 %MX593 | C/V #11 M037.1 %MX593 | C/V #11 M037.1 %MX593 | C/V #11 M037.1 %MX593 | C/V #11 M037.1 %MX593
57 |  | WCS 값 | PLC ID Shift 결과 : JOB 이 반출 위치로 이동 | C/V #11 R0102 %RB516 | C/V #11 R0102 %RB516 | C/V #11 R0102 %RB516 | C/V #11 R0102 %RB516 | C/V #11 R0102 %RB516 | EQP_TASK | CvThread.cs | CvStatusScenario()
58 |  | EQP BIT OFF | 입출고대 반출 완료 (작업자 회수) | C/V #11 M037.1 %MX593 | C/V #11 M037.1 %MX593 | C/V #11 M037.1 %MX593 | C/V #11 M037.1 %MX593 | C/V #11 M037.1 %MX593 | IO_TASK HOST_TASK | cThread_SCH.cs CCliWork.cs | CompleteCV() GetJobCompleteReport()
반송 시나리오 2. S/C → 입출고대 #22 출고 (랙 → S/C → 통로 → RGV → C/V #11)
실선 → 비트 ON/OFF · 점선 → D/R 워드 값 기록·확인 · 왼쪽 끝 = M/D/R 영역 문서표기 + 실제 접근주소 (S/C #1 기준)
EQP (설비 / PLC)
ECS (WCS)
① S/C #1 — 17 스텝
D0160 %DW256
1. IDLE=1 확인
M096.0 %MX1536
2. Transfer Command Req’ (WCS 지시)
D0320 %DW768
3. Transfer Command Data - From (랙 셀)
D0323 %DW771
4. Transfer Command Data - To (하역 포트)
D0326 %DW774
5. Transfer Command Data - Job No
M048.0 %MX768
6. Pallet Presence ON (S/C 적재)
R0300 %RB1536
7. On S/C - 탑재 화물번호
M049.0 %MX784
8. Load Complete ON
M096.1 %MX1537
9. Load Complete Ack ON (WCS)
D0166 %DW262
10. S/C 현재위치(열/연/단)
M049.0 %MX784
11. Load Complete OFF
M048.0 %MX768
12. Pallet Presence OFF (통로 C/V 하역 완료)
M049.1 %MX785
13. Unload Complete ON
M096.2 %MX1538
14. Unload Complete Ack ON (WCS)
D0163 %DW259
15. Transfer Complete Location
M049.1 %MX785
16. Unload Complete OFF
D0160 %DW256
17. IDLE 복귀
② C/V #2 — 15 스텝
M019.1 %MX305
18. S/C측 Pallet Exist ON (S/C 하역 완료)
M018.4 %MX292
19. Load Complete #2 ON
M081.4 %MX1300
20. Load Complete Ack #2 ON (WCS)
M018.4 %MX292
21. Load Complete #2 OFF
D0301 %DW481
22. 방향 확인 - 출고 '1'
R0012 %RB36
23. JOB NO 기록 (S/C측 위치)
M019.1 %MX305
24. S/C측 Pallet Exist OFF (ID Shift)
M019.0 %MX304
25. RGV측 Pallet Exist ON (도착)
R0010 %RB32
26. PLC ID Shift 결과 : JOB 이 RGV측으로 이동
M018.6 %MX294
27. W.O 보고 (RGV Call)
M019.0 %MX304
28. RGV측 Pallet Exist OFF (RGV Load 완료)
M018.1 %MX289
29. Unload Complete #1 ON (RGV 픽업)
M081.1 %MX1297
30. Unload Complete Ack #1 ON (WCS)
M018.1 %MX289
31. Unload Complete #1 OFF
M018.6 %MX294
32. W.O OFF
③ RGV #1 — 16 스텝
D0210 %DW336
33. IDLE=1 확인
M101.0 %MX1616
34. Transfer Command Req’ (WCS 지시)
D0370 %DW848
35. Transfer Command Data - From (픽업 포트)
D0373 %DW851
36. Transfer Command Data - To (입출고대 #21)
D0376 %DW854
37. Transfer Command Data - Job No
M058.0 %MX928
38. Pallet Presence ON (RGV 적재)
R0310 %RB1568
39. On RGV - 탑재 화물번호
M059.0 %MX944
40. Load Complete ON
M101.1 %MX1617
41. Load Complete Ack ON (WCS)
D0213 %DW339
42. Transfer Complete Location
M059.0 %MX944
43. Load Complete OFF
M058.0 %MX928
44. Pallet Presence OFF (하역)
M059.1 %MX945
45. Unload Complete ON
M101.2 %MX1618
46. Unload Complete Ack ON (WCS)
M059.1 %MX945
47. Unload Complete OFF
D0210 %DW336
48. IDLE 복귀
④ C/V #11 — 10 스텝
M037.0 %MX592
49. 입출고대 RGV측 Pallet Exist ON (RGV 하역)
M036.2 %MX578
50. Load Complete #1 ON
M090.2 %MX1442
51. Load Complete Ack #1 ON (WCS)
M036.2 %MX578
52. Load Complete #1 OFF
D0310 %DW490
53. 방향 확인 - 출고 '1'
R0100 %RB512
54. JOB NO 기록 (RGV측 위치)
M037.0 %MX592
55. RGV측 Pallet Exist OFF (ID Shift)
M037.1 %MX593
56. 입출고대 반출 위치 Pallet Exist ON (도착)
R0102 %RB516
57. PLC ID Shift 결과 : JOB 이 반출 위치로 이동
M037.1 %MX593
58. 입출고대 반출 완료 (작업자 회수)